## OUTFUN500
Category | Op Center | Circuit | Time Off | Time On | Outage ID | Device & Ph | Clearing Device | Resp. System | Cause (IEEE) | Failure Mode | AT/D/M | Eq. Code | Manuf./ Species | Cnt | Planned Outages | WE | # Cust | Ckt Cust | Dur | Fault Location | Crew Remarks | Additional Remarks
Sub/T - MED | Chapel Hill rlw2159 | EFLAND - 19241202 | 4/19/2019 16:10 | 4/19/2019 18:14 | 11181871 | S-CKT - ABC Size: Class 3 FID: 38358957 | 01 Feeder Breaker/Recl in Substa | 00 Substation | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | PT PINE | 25 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,784 | 1789 | 124 |  | Limb across all three phases near intersection of Redman Rd. and US 70 | rlw2159-(MED DAY) CREW REMOVED PINE LIMB FROM 3 PHASE PRIMARY. PINE LIMB APRROXIMATELY 3" IN DIAMETER AND 25' FROM CENTER LINE. ~~~ 4/23/2019 ¦ rlw2159 ¦ Investigative Action
Sub/T | Asheboro i25781 | ASHEBORO SOUTH 115KV - DIXIE DRIVE 23KV | 4/26/2019 17:42 | 4/26/2019 18:34 | 5040870 | SOURCE - ABC FID: T0950B04 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | TF Tree fails, defective | DR Roots rotten/defective | NA | OA Oak | 53 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,764 | 1760 | 52 | Metered Point~T0950B04 | Transmission Transmission Line Outage Unknown At Time Of Outage | JWW// During high wind storm crew found oak tree on line at str 182-183, removed oak tree and found no damage to conductor. Tree was 53' from center line. ~~~ 5/1/2019 ¦ i25781 ¦ Investigative Action
Sub/T | Asheboro i25781 | ASHEBORO SOUTH 115KV - ASHEBORO SOUTH 23KV | 4/26/2019 17:42 | 4/26/2019 18:34 | 5040878 | SOURCE - ABC FID: T0950B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | TF Tree fails, defective | DR Roots rotten/defective | NA | OA Oak | 53 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,841 | 1839 | 52 | Switch~T0950B03 | Transmission Transmission Line Outage Unknown At Time Of Outage | JWW// During high wind storm crew found oak tree on line at str 182-183, removed oak tree and found no damage to conductor. Tree was 53' from center line. Pictures available. ~~~ 5/1/2019 ¦ i25781 ¦ Investigative Action
Sub/T | Asheboro i25781 | ASHEBORO SOUTH 115KV - MCDOWELL ROAD 23KV | 4/26/2019 17:42 | 4/26/2019 18:34 | 5040805 | SOURCE - ABC FID: T0950B05 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | TF Tree fails, defective | DR Roots rotten/defective | NA | OA Oak | 53 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,446 | 1444 | 52 | Switch~T0950B05 | Transmission Transmission Line Outage Unknown At Time Of Outage | JWW// During high wind storm crew found oak tree on line at str 182-183, removed oak tree and found no damage to conductor. Tree was 53' from center line. Pictures available. ~~~ 5/1/2019 ¦ i25781 ¦ Investigative Action
Sub/T | Asheboro i25781 | BISCOE 115KV - HIGHWAY 220 23KV | 4/26/2019 17:44 | 4/26/2019 17:50 | 5040602 | SOURCE - ABC FID: T0990B02 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | TF Tree fails, defective | DR Roots rotten/defective | NA | OA Oak | 53 | F2 Forced Outage | 04 Wind, Rain and Lightning | 899 | 901 | 6 | STR 182-183 | Transmission Transmission Line Outage Unknown At Time Of Outage | JWW// During high wind storm crew found oak tree on line at str 182-183, removed oak tree and found no damage to conductor. Tree was 53' from center line. ~~~ 5/1/2019 ¦ i25781 ¦ Investigative Action
Sub/T | Asheboro i25781 | BISCOE 115KV - STAR NORTH 23KV | 4/26/2019 17:44 | 4/26/2019 17:50 | 5040606 | SOURCE - ABC FID: T0990B01 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | TF Tree fails, defective | DR Roots rotten/defective | NA | OA Oak | 53 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,007 | 1011 | 6 | STR 182-183 | Transmission Transmission Line Outage Unknown At Time Of Outage | JWW// During high wind storm crew found oak tree on line at str 182-183, removed oak tree and found no damage to conductor. Tree was 53' from center line. ~~~ 5/1/2019 ¦ i25781 ¦ Investigative Action
Sub/T | Asheboro i25781 | BISCOE 115KV - BISCOE 23KV | 4/26/2019 17:45 | 4/26/2019 17:51 | 5040615 | SOURCE - ABC FID: T0990B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | TF Tree fails, defective | DR Roots rotten/defective | NA | OA Oak | 53 | F2 Forced Outage | 04 Wind, Rain and Lightning | 562 | 578 | 6 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | JWW// During high wind storm crew found oak tree on line at str 182-183, removed oak tree and found no damage to conductor. Tree was 53' from center line. Pictures available. ~~~ 5/1/2019 ¦ i25781 ¦ Investigative Action
Sub/T | Durham dlm4375 | HOPE VALLEY - 14061209 | 5/8/2019 10:33 | 5/8/2019 12:16 | 11208657 | S-CKT - ABC Size: Class 3 FID: 38355597 | 00 Substation device | 00 Substation | 28 Other Cause | D1 Broken/Malfunctioning | MP Porcelain | HW Hardware |  |  | F2 Forced Outage | 00 Calm | 2,021 | 2026 | 103 | 3 BELLS FAILED ON STEEL DISTRIBUTION SIDE IN SUBST | CMPL 2019-05-08 12:21:00 by BNADCOC RMK: LOCK OUT - TARGET CG & FMAG 7006 - ECC SENDING STATION TECH DUE TO HIGH FAULT MAG | dlm4375 We had 3 dead end bells on the steel inside the substation on distribution side explode/break. bells tracked down to the steel/metal framing and caught fire. ~~~ 5/9/2019 ¦ dlm4375 ¦ Investigative Action
Sub/T | Cary c72037 | FUQUAY BELLS LAKE 230KV - HILLTOP 23KV | 5/23/2019 13:58 | 5/23/2019 15:20 | 5049261-2 | SOURCE - ABC FID: PNU79_104307160 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J5 Snake |  | F2 Forced Outage | 00 Calm | 1,022 | 2391 | 82 | Switch~T4866B01 | Transmission Substation Equipment Outage Animal/Bird (Comments) SNAKE | MHS- Crew arrived to find a 5' black snake had made it's way to the top timber of the substation and crawled thru the animal guard onto the disconnect switch causing a phase to ground fault on the Optimist Farm FCB opening the high side switch of the Fuquay Bells Lake substation, causing an outage on all 6 FCB. ~~~ 5/24/2019 ¦ c72037 ¦ Investigative Action
Sub/T | Cary c72037 | FUQUAY BELLS LAKE 230KV - HILLTOP 23KV | 5/23/2019 13:58 | 5/23/2019 14:45 | 5049261-1 | SOURCE - ABC FID: T4866B04 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J5 Snake |  | F2 Forced Outage | 00 Calm | 1,340 | 2391 | 47 | Switch~T4866B01 | Transmission Substation Equipment Outage Animal/Bird (Comments) SNAKE | MHS- Crew arrived to find a 5' black snake had made it's way to the top timber of the substation and crawled thru the animal guard onto the disconnect switch causing a phase to ground fault on the Optimist Farm FCB opening the high side switch of the Fuquay Bells Lake substation, causing an outage on all 5 FCB. ~~~ 5/24/2019 ¦ c72037 ¦ Investigative Action
Sub/T | Cary c72037 | FUQUAY BELLS LAKE 230KV - OPTIMIST FARM 23KV | 5/23/2019 13:58 | 5/23/2019 14:51 | 5049259 | SOURCE - ABC FID: T4866B01 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J5 Snake |  | F2 Forced Outage | 00 Calm | 1,878 | 1880 | 53 | t4866b01 | Transmission Substation Equipment Outage Animal/Bird (Comments) SNAKE ON OPTIMIST FARM FCB | MHS- Crew arrived to find a 5' black snake had made it's way to the top timber of the substation and crawled thru the animal guard onto the disconnect switch causing a phase to ground fault on the Optimist Farm FCB opening the high side switch of the Fuquay Bells Lake substation, causing an outage on all 6 FCB. ~~~ 5/24/2019 ¦ c72037 ¦ Investigative Action
Sub/T | Cary c72037 | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 5/23/2019 13:58 | 5/23/2019 14:46 | 5049260 | SOURCE - ABC FID: T4866B05 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J5 Snake |  | F2 Forced Outage | 00 Calm | 2,908 | 2927 | 48 | Switch~T4866B01 | Transmission Substation Equipment Outage Animal/Bird (Comments) SNAKE ON OPTIMIST FARM FCB | MHS- Crew arrived to find a 5' black snake had made it's way to the top timber of the substation and crawled thru the animal guard onto the disconnect switch causing a phase to ground fault on the Optimist Farm FCB opening the high side switch of the Fuquay Bells Lake substation, causing an outage on all 5 FCB. ~~~ 5/24/2019 ¦ c72037 ¦ Investigative Action
Sub/T | Cary c72037 | FUQUAY BELLS LAKE 230KV - STATE ROAD 1010 23KV | 5/23/2019 13:59 | 5/23/2019 15:01 | 5049297 | SOURCE - ABC FID: T4866B03 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J5 Snake |  | F2 Forced Outage | 00 Calm | 1,935 | 1937 | 62 | Switch~T4866B01 | Transmission Substation Equipment Outage Animal/Bird (Comments) SNAKE ON OPTIMIST FARM FCB | MHS- Crew arrived to find a 5' black snake had made it's way to the top timber of the substation and crawled thru the animal guard onto the disconnect switch causing a phase to ground fault on the Optimist Farm FCB opening the high side switch of the Fuquay Bells Lake substation, causing an outage on all 5 FCB. ~~~ 5/24/2019 ¦ c72037 ¦ Investigative Action
Sub/T | Cary c72037 | FUQUAY BELLS LAKE 230KV - PENNY ROAD 23KV | 5/23/2019 14:00 | 5/23/2019 14:45 | 5049376 | SOURCE - ABC FID: T4866B02 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J5 Snake |  | F2 Forced Outage | 00 Calm | 1,037 | 1892 | 45 | Switch~T4866B01 | Transmission Substation Equipment Outage Animal/Bird (Comments) SNAKE ON OPTIMIST FARM FCB | MHS- Crew arrived to find a 5' black snake had made it's way to the top timber of the substation and crawled thru the animal guard onto the disconnect switch causing a phase to ground fault on the Optimist Farm FCB opening the high side switch of the Fuquay Bells Lake substation, causing an outage on all 6 FCB. ~~~ 5/24/2019 ¦ c72037 ¦ Investigative Action
Sub/T | Durham rlw2159 | ENO - 14102401 | 6/9/2019 03:32 | 6/9/2019 04:54 | 11242823 | S-CKT - ABC Size: Class EX FID: 38355777 | 00 Substation device | OH Distribution Line Overhead | 11 Unknown Cause | ED Erosion/Washout | 14 Closed Breaker | 29 Conductor, bare | OA Oak | 25 | F2 Forced Outage | 17 Wind and Rain | 948 | 947 | 82 | Cornwallis 1 mile from murphy school rd | CMPL 2019-06-09 05:00:00 by VDB7113 RMK: CKT L/O : 06/09/19 03:32:09 BC T BC T(51) 4423 /. No Problem found. TL 516 VB | rlw2159-50' tall oak tree approximately 14" through the center fell from 25' out of the ROW burning down the middle phase of 336 primary on Cornwallis Rd about 1 mile from Murphy School Rd going towards Kerley Rd. The root system couldn't hold the tree anymore due to what appears to be erosion. The fault bypassed the 140 L Recloser and took out the station breaker. This recloser has given problems and is in scheduling to be c/o to a Viper. Outage ticket# 11242915 is associated with this outage. ~~~ 6/13/2019 ¦ rlw2159 ¦ Completion Codes or Remarks
Sub/T | Durham rlw2159 | FAIRNTOSH - 14142410 | 6/9/2019 23:19 | 6/10/2019 03:09 | 11244359 | S-CKT - ABC Size: Class 2 FID: 38356473 | 00 Substation device | OH Distribution Line Overhead | 20 Equipment failure | 19 Lightning strike | 52 Restored From Alternate Sourc | 46 R Regulator, Station 3 Ph |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 3,569 | 3589 | 230 |  | SUBSTATION OUTAGE - BANK 3 LOW TENSION BUS BAR HAD AN INSULATOR THAT FAILED - BANK 3 INCLUDES STATION EXIT FEEDERS 2407, 2409 & 2410 - LOAD WAS MOVED TO AX BREAKER USING THE TRANSFER BUS. ALL CUSTOMERS RESTORED - MONITOR LOAD ON 24AX | rlw2159-(storm in area)Lightning hit an insulator inside the substation bank 3 low tension buss. Insulator was changed out on 6/10 and returned to normal on 6/11. ~~~ 6/11/2019 ¦ rlw2159 ¦ Investigative Action
Sub/T | Durham rlw2159 | FAIRNTOSH - 14142407 | 6/9/2019 23:19 | 6/10/2019 03:09 | 11244362 | S-CKT - ABC Size: Class 3 FID: 38356449 | 00 Substation device | OH Distribution Line Overhead | 20 Equipment failure | 19 Lightning strike | 52 Restored From Alternate Sourc | 46 R Regulator, Station 3 Ph |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,905 | 1905 | 230 |  | SUBSTATION OUTAGE - BANK 3 LOW TENSION BUS BAR HAD AN INSULATOR THAT FAILED - BANK 3 INCLUDES STATION EXIT FEEDERS 2407, 2409 & 2410 - LOAD WAS MOVED TO AX BREAKER USING THE TRANSFER BUS. ALL CUSTOMERS RESTORED - MONITOR LOAD ON 24AX | rlw2159-(storm in area)Lightning hit an insulator inside the substation bank 3 low tension buss. Insulator was changed out on 6/10 and returned to normal on 6/11. ~~~ 6/14/2019 ¦ rlw2159 ¦ Investigative Action
Veg | Garner c72037 | GARNER WHITE OAK 230KV - WHITE OAK 24KV | 4/5/2019 17:06 | 4/5/2019 17:57 | 5029518-1 | OCB - ABC FID: T4730B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | M2 ACSR | 29 Conductor, bare | BP Bradford Pear | 0 | F2 Forced Outage | 02 Rain | 1,875 | 1912 | 51 | X595 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None work completed by duke crew. restored to normal | MHS- Line tech was called out with the White Oak FCB locked out, DCC had no fault locations. As line tech was riding out the line he observed fire trucks turning down a road. He followed them to a line down at X585BJ. He rode to the Sectionalizer at X558 and tried to open, after several times and bending the bracket he gave up and had the crew do a line cut at X587BJ and having DCC re-energizing the FCB getting all but 22 customers back on ~~~ 4/8/2019 ¦ c72037 ¦ Investigative Action
Veg | Sanford i25781 | SANFORD HORNER BLVD. 230KV - GULF 23KV | 4/8/2019 16:36 | 4/8/2019 18:28 | 5030384 | RECLOSER - ABC FID: T675AC_2361168 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DC Internal stem decay | NA | OA Oak | 36 | F2 Forced Outage | 04 Wind, Rain and Lightning | 556 | 1851 | 112 | T811AC | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None trees on lines | JWW// On 4/8/19 at 04:36pm an oak tree limb broke off and fell across all three phases locking out 3 pole top reclosers at T675AC causing 556 customers to loose power. When the service tech arrived he removed tree no damage was done to conductor and then energized the reclosers at 06:28pm restoring power to all 556 customers. ~~~ 4/10/2019 ¦ i25781 ¦ Investigative Action
Veg | Chatham County AArias | PITTSBORO 230KV - NORTHWOOD 23KV | 4/8/2019 16:55 | 4/8/2019 18:07 | 5030405 | OCB - ABC FID: T2250B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | MP Maple | 25 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,207 | 2225 | 72 | Node~1093160 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON PRIMARY AT AG90AF | aarias// storm in area. Large live maple limb broke from 25 ft away and fell on our lines. Limb was removed and circuit re-energized. No equipment damage ~~~ 4/15/2019 ¦ AArias ¦ Investigative Action
Veg | Cary AArias | CARY REGENCY PARK 230KV - SOUTHCHASE 23KV | 4/12/2019 19:22 | 4/12/2019 20:03 | 5032647-1 | OCB - ABC FID: T4599B24 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 37 Removed Limb or Tree From Lin | NA | UN Unknown Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,500 | 1488 | 41 | Line~6458K_6459K_2626015 | Tree/Vegetatn Tree/Limb Growth None line down | aarias// storm in area. Line runs within transmission corridor and corridor is clear. It's most likely to have been caused by vegetation, but exact cause of outage is undetermined ~~~ 4/16/2019 ¦ AArias ¦ Investigative Action
Veg | Garner c72037 | DUNCAN 230KV - DUNCAN 24KV | 4/12/2019 23:35 | 4/13/2019 01:36 | 5032829 | RECLOSER - BC FID: J805BH_103783585 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | NA | PT PINE | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 999 | 2626 | 121 | J805BH | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE FELL ON ALL 3 PHASES | MHS-A 8" dia. defective pine tree broke about 10' above ground level falling across all 3 phases of primary locking out Recloser J805BH, crew cleared tree from line and had DCC reenergize Recloser ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Cary AArias | RALEIGH OAKDALE 230KV - ROYLENE 23KV | 4/15/2019 00:47 | 4/15/2019 20:59 | 5033619 | OCB - ABC FID: T5136B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TL Tree fails, NAC | DE Erosion/poor enviornment | PP Pole | OA Oak | 55 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,860 | 2780 | 1212 | aarias// GP35K | Missing Missing Missing | aarias// storm in area. Large 90 ft tall live oak tree uprooted due to poor soil and fell on our lines from 50 ft away. Took down 4 spans of double circuit lines, and broke 3 poles. Poles replaced and lines repaired. No follow up needed. Related to 5033621-1 (Farm Gate outage) ~~~ 4/16/2019 ¦ AArias ¦ Investigative Action
Veg - MED | Cary C80721 | RALEIGH OAKDALE 230KV - FARM GATE 23KV | 4/15/2019 00:50 | 4/15/2019 04:34 | 5033621-1 | OCB - ABC FID: T5136B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DE Erosion/poor enviornment | PP Pole | OA Oak | 55 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,234 | 2295 | 224 | aarias// GP35K | Tree/Vegetatn Limb Fell from Outside Right of Way None | aarias// storm in area. Large 90 ft tall live oak tree uprooted due to poor soil and fell on our lines from 50 ft away. Took down 4 spans of double circuit lines, and broke 3 poles. Damage isolated and downstream customers backfed from Plaza West 23KV while repairs were underway. No further work needed. Related to 5033619 (Roylene outage) LWB - update based upon FMS and CYME. Review with BL. ~~~ 4/16/2019 ¦ C80721 ¦ Investigative Action
Veg - MED | Cary AArias | CARY REGENCY PARK 230KV - SOUTHCHASE 23KV | 4/15/2019 00:51 | 4/15/2019 02:20 | 5033635-1 | OCB - ABC FID: T4599B24 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | UN Unknown Species | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,474 | 1488 | 89 | aarias// 6636K | Tree/Vegetatn Limb Fell from Outside Right of Way None | aarias// storm in area. Tree limb fell from outside ROW, could not be found during inspection. ROW is clear, feeder was proactively trimmed in 2015. Veg management to follow up and cut down potential dead hazard tree on edge of ROW ~~~ 4/17/2019 ¦ AArias ¦ Investigative Action
Veg - MED | Cary AArias | CARY 230KV - WEST CHATHAM STREET 23KV | 4/15/2019 00:53 | 4/15/2019 02:58 | 5033643 | OCB - ABC FID: T4600B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 14 Closed Breaker | NA | UN Unknown Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 3,411 | 3395 | 125 | Line~1BLN31_8575K_112297297 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree limb at 1bln31 on 2 phases | aarias// storm in area. Tree limb across 2 phases, limb not found, so origin and species could not be determined. No equipment damage ~~~ 4/15/2019 ¦ AArias ¦ Investigative Action
Veg - MED | Garner c72037 | HOLLY SPRINGS 230KV - SURRY RIDGE 24KV | 4/15/2019 01:16 | 4/15/2019 04:01 | 5033689 | OCB - ABC FID: T4795B22 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect | NA | CR Eastern Redcedar |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,410 | 1448 | 165 | B044K | Tree/Vegetatn Tree/Limb Growth None tree b044q | MHS- Crew found trees burning in primary at B044K which locked out the SURRY RIDGE feeder. crews trimmed trees back and had DCC re-energize the FCB ~~~ 5/14/2019 (29 days) ¦ c72037 ¦ Investigative Action
Veg - MED | Cary omshistproc | CARY 230KV - CARY 23KV | 4/15/2019 05:47 | 4/15/2019 11:55 | 5060310 | LINE CUT - ABC FID: Line Cut-639999 | 09 Jumper/wire cut/open | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 02 Rain | 802 | 1574 | 368 | Node~1464026 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
Veg - MED | Cary C80721 | CARY 230KV - CARY 23KV | 4/15/2019 14:50 | 4/15/2019 16:23 | 5060305-2 | FUSE - ABC FID: J602K_2646519 | 03 Line Fuse | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,604 | 1574 | 93 | Load~8389K | Tree/Vegetatn Limb Fell from Outside Right of Way None | LWB - update based upon FMS and Cyme - reviewed in detail. assist BL ~~~ 6/7/2019 (53 days) ¦ C80721 ¦ No Action Required
Veg - MED | Cary omshistproc | CARY 230KV - CARY 23KV | 4/15/2019 14:50 | 4/15/2019 16:23 | 5060305-1 | OCB - ABC FID: T4600B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,460 | 1574 | 93 | Load~8389K | Tree/Vegetatn Limb Fell from Outside Right of Way None | ... NO OUTAGE REVIEW INFO
Veg - MED | Garner c72037 | HOLLY SPRINGS 230KV - RHAMKATTE 24KV | 4/19/2019 11:13 | 4/19/2019 12:38 | 5035775-1 | SWITCH - ABC FID: 1CHB71_114201583 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DV Visible stem decay | NA | BR Birch, river | 10 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,364 | 1550 | 85 | U056BH | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree @ u056bh | MHS- A 8" in DIA. defective birch tree broke about 20' above ground level falling across all 3 phases locking out the FCB. Crew did switching to get 1364 customers back on by back feeding from the Sunset Ridge North the remaining 649 customers stayed off till crew cut and removed limb. Crew then had DCC reenergize FCB. ~~~ 4/24/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Garner c72037 | CLAYTON 115KV - GLENHAVEN 24KV | 4/19/2019 11:24 | 4/19/2019 12:36 | 5035806 | OCB - ABC FID: T5640B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 33 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,586 | 1727 | 72 | Node~1865628 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Dead pine fell into feeder at GG12BJ, cut tree off line. kv Dead pine fell into feeder at GG12BJ, cut tree off line. kv | MHS- A dead pine tree 16" in dia. fell over on to the Glenhaven circuit locking out the FCB. crew rode out line finding tree at DIS# GG12BJ. Crew cut tree off of line and had DCC close back in the FCB. ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Cary c72037 | FUQUAY BELLS LAKE 230KV - STATE ROAD 1010 23KV | 4/19/2019 11:45 | 4/19/2019 13:31 | 5035877 | RECLOSER - A C FID: 100795_104307157 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | NA | CR Eastern Redcedar | 15 | F2 Forced Outage | 04 Wind, Rain and Lightning | 696 | 1937 | 106 | 7532K | Tree/Vegetatn Limb Fell from Inside Right of Way None Limb laying across A and C phase @ 7532K | MHS- A defective cedar tree fell over at the root ball laying across A and C phase locking out recloser 100795. just them 2 phases locked out. crew removed tree and had DCC reenergize the recloser. ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Cary c72037 | CARY TRIANGLE FOREST 230KV - CHURCHILL 23KV | 4/19/2019 11:53 | 4/19/2019 14:11 | 5035893-1 | OCB - ABC FID: T4605B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect | NA | HK Hickory |  | F2 Forced Outage | 00 Calm | 2,037 | 1627 | 138 | Between DIS# CBA83 and CDL98 | Tree/Vegetatn Tree/Limb Growth None TREE CBA83 CDL98 | MHS- feeder locked out due to trees growing into primary. crews trimmed trees back and had DCC close back in the FCB ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Durham dlm4375 | FAIRNTOSH - 14142407 | 4/19/2019 15:10 | 4/19/2019 17:48 | 11181370 | RCL - ABC Size: 200 4E FID: 39011197 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DA Damaged |  | EL Elm | 21 | F2 Forced Outage | 04 Wind, Rain and Lightning | 930 | 1905 | 158 | lakeview and amirrilas | CMPL 2019-04-19 17:53:00 by WJAMES RMK: 200 4E-LIMB ON LINE AT LAKEVIEW AND AMARYLLIS- | dlm4375 med day..recloser 2004E opened due to Elm tree limb fails 21' from center line ,2 1/2 " diameter, looks like when it was growing it was knicked or maybe damaged at sometime...tree located at Lakeview and Amirilas... crew removed tree limb from ovhd primary...primary did not fall, primary ok.....this made circuit blink see 11181356 ~~~ 4/22/2019 ¦ dlm4375 ¦ Investigative Action
Veg - MED | Chatham County c72037 | SILER CITY 115KV - SILER CITY NORTH 24KV | 4/19/2019 15:37 | 4/19/2019 16:18 | 5036538-1 | RECLOSER - ABC FID: 3190AF_103299423 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | M6 CCA | P1 Pole, Creosote | PT PINE | 39 | F2 Forced Outage | 04 Wind, Rain and Lightning | 649 | 2576 | 41 | 5559AF | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None trees on line has broken pole 5559AF trees on line has broken pole 5559AF | MHS- A 16" in DIA. live pine tree fell 39' from C/L across all 3 phases of primary, tearing down primary and open wire secondary breaking pole 5559AF. Crew did some switching and line cut to get all but 186 customers on by 11:40 pm. the 186 customers had to stay off till job was completed. ~~~ 4/29/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Chapel Hill rlw2159 | JAMES ST - 19031206 | 4/19/2019 16:08 | 4/20/2019 00:52 | 11181834 | RCL - ABC Size: 200 L FID: 39007375 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 29 Permanent Repair | CR Crossarm | HW HARDWOOD |  | F2 Forced Outage | 11 Tornado/Wind Shear/Microburst | 518 | 1758 | 524 | 1501 Dairyland | 200 L SOLAR SITE OUT | rlw2159-(TORNADO MED DAY) Poplar tree tore down 2 spans of #4 cu pri/neut and broke crossarm. ~~~ 4/22/2019 ¦ rlw2159 ¦ Completion Codes or Remarks
Veg - MED | Chapel Hill rlw2159 | BINGHAM - 19251210 | 4/19/2019 16:17 | 4/20/2019 00:54 | 11183193 | SOH - ABC Size: 600 Line Disconnect FID: 39041118 | 08 Disconnect | OH Distribution Line Overhead | EA Weather | 03 Tree (Vegetation) | DA Damaged | 29 Conductor, bare | HW HARDWOOD | 30 | F2 Forced Outage | 11 Tornado/Wind Shear/Microburst | 1,591 | 1660 | 517 | HWY 70-A and Meadowland DR | CMPL 2019-04-20 00:50:00 by CRBARWI RMK: opened FAC ID 39041118 will Ground down lines then verify we can re energize station breaker, grounds hung at meadow land dr, found a broken insulator at tuscorora. Tornado caused trees to fall on line. Repairs mad | rlw2159-(MED DAY)broken insulator at tuscorora, also had 1 span of primary down and 6 broke insulators @ Meadowlands Dr & HWY 70A. Disconnects at FID# 39041118 were closed and circuit re-energized. Associated tickets are 11181938(blink), 11181954(circuit lockout) & 11183691(open circuit to close disconnects) ~~~ 4/22/2019 ¦ rlw2159 ¦ Investigative Action
Veg - MED | Durham rlw2159 | POPE ROAD - 14082404 | 4/19/2019 16:39 | 4/19/2019 16:59 | 11182182 | S-CKT - ABC Size: Class 2 FID: 38355933 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 05 Planned (IEEE) | 26 Vines | 14 Closed Breaker |  | 28 Other Species |  | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 3,236 | 3245 | 20 | DIP POLE AT NORTHAMPTON AND OLD CHAPEL HILL | emergeny drop cleaning vines and circuit started arching .. dropped to complete work | rlw2159-(MED DAY)crew had to drop circuit to clean vines off pole. Vines started arcing while trying to remove them. ASSOCIATED BLINK TICKET# 11182149 ~~~ 4/24/2019 ¦ rlw2159 ¦ Investigative Action
Veg - MED | Garner c72037 | FUQUAY 230KV - HOLLAND ROAD 23KV | 4/19/2019 17:07 | 4/19/2019 18:48 | 5037061-1 | OCB - ABC FID: T4710B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | NA | OB Oak, white | 27 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,059 | 2682 | 101 | 9Q936 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE AT 9Q936 | MHS- 18" in dia. defective white oak broke about 30 above ground level falling across all 3 phases at air break switch locking out FCB. Crew did switching to get all but 578 customers back on. Crew cut tree in the clear and had DCC reenergize the FCB ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Garner c72037 | FUQUAY 230KV - HOLLAND ROAD 23KV | 4/19/2019 17:07 | 4/19/2019 19:42 | 5037061-4 | RECLOSER - ABC FID: R224BH_104434583 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | NA | OB Oak, white | 27 | F2 Forced Outage | 04 Wind, Rain and Lightning | 578 | 2682 | 155 | 9Q936 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE AT 9Q936 | MHS- 18" in dia. defective white oak broke about 30 above ground level falling across all 3 phases at air break switch locking out FCB. Crew did switching to get all but 578 customers back on. Crew cut tree in the clear and had DCC reenergize the FCB ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Cary c72037 | RALEIGH SOUTH 115KV - AVENT FERRY 23KV | 4/19/2019 17:15 | 4/19/2019 18:08 | 5037110-1 | SWITCH - ABC FID: 0680K_2740029 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | P2 Pole, CCA | OA Oak | 15 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,057 | 1846 | 53 | CC026 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None broke feeder pole CC026 need tree crew//55c3 3 spans 477 down. | MHS- adding outage 5037114 customer count to this outage because the other phase went out only 6 sec. behind the first 2. a 24" in dia. defective oak tree fell over pinning guys against pole and breaking top of pole out. crew did switching to get as many customers back on as possible but due to tree crews lack of experience the crew called off the job till the next morning. with new tree crew the job was completed the next day. ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 4/19/2019 17:19 | 4/19/2019 17:56 | 5037134-2 | OCB - ABC FID: T4720B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TL Tree fails, NAC | M6 CCA | P1 Pole, Creosote | PT PINE | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,373 | 2735 | 37 | T067BJ | Missing Missing Missing | MHS- When feeder locked out SHT closed in recloser DB57BJ getting on 1357 customers back on in less than 2 min. the remaining 1373 stayed off till the crew could replace pole and get wire back up. rode job out, customer must have cleaned up could find no debris or where it broke off at. ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Veg - MED | Garner omshistproc | MILBURNIE 230KV - BELTLINE 23KV | 4/19/2019 17:26 | 4/19/2019 21:36 | 5037213 | OCB - ABC FID: T5000B44 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,098 | 1097 | 250 | Node~2070266 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None trees leaning on line at dis# B661BK (Raleigh Ops side) | ... NO OUTAGE REVIEW INFO
Veg | Durham rlw2159 | GARRETT RD - 14202414 | 4/23/2019 12:51 | 4/23/2019 13:59 | 11186910 | S-RCL - ABC Size: 560 WVE FID: 38998845 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | 26 Vines | 37 Removed Limb or Tree From Lin | 43 Recloser, Electronic |  |  | F2 Forced Outage | 00 Calm | 632 | 1926 | 68 | hope valley rd and s roxboro rd. | CMPL 2019-04-23 14:31:00 by LEMCKIN RMK: RECLOSER LOCKOUT, TARGETS BG FAULT UNKNOWN. removed vines from recloser | rlw2159-crew had to remove vines from recloser and then re-energize. ASSOCIATED BLINK TICKET(11186884) ~~~ 4/24/2019 ¦ rlw2159 ¦ Investigative Action
Veg | Garner c72037 | DUNCAN 230KV - DUNCAN 24KV | 4/26/2019 02:40 | 4/26/2019 04:38 | 5039918-1 | RECLOSER - ABC FID: J805BH_103783585 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | 29 Conductor, bare | OB Oak, white | 45 | F2 Forced Outage | 00 Calm | 723 | 2626 | 118 | K649BH | Tree/Vegetatn Limb Fell from Inside Right of Way None work completed and restored | MHS- A 30" in DIA. defective white oak tree split and fell across all 3 phases of primary, taking down 5 spans. Crews opened up solid blades at K378BH had DCC reenergize recloser at J805BH getting 723 customers back on then they did a line cut to get another 207 customers on the rest stayed off till repairs were done. Looking to put a recloser where solid blades are. ~~~ 4/29/2019 ¦ c72037 ¦ Investigative Action
Veg | Chapel Hill rlw2159 | EASTGATE RET - 19021208 | 4/27/2019 18:35 | 4/27/2019 20:43 | 11197960 | S-CKT - ABC Size: Class 1 FID: 38359209 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | DE Erosion/poor enviornment | P1 Pole, Creosote | OA Oak | 25 | F2 Forced Outage | 03 Wind | 774 | 800 | 128 | 412 clayton tree on lines , broken pole. | CMPL 2019-04-27 22:01:00 by DKM3045 RMK: CKT LOCKOUT/FMAG 2968 A C TRIP 50/MOST LIKELY FAULT LOCATION NEAR FACID 38587733 OLD OXFORD AT MARKHAM DR - TREE REPORTED ON LINE AT 412 CLAYTON / ALSO AT 2020 MARKHAM | rlw2159 windy condition...large co dominate oak approximately 3" round at base,25' feet from center line fell due to wet area and defective base-- CKT LOCKOUT/FMAG 2968 A C TRIP 50/MOST LIKELY FAULT LOCATION NEAR FACID 38587733 OLD OXFORD AT MARKHAM DR - TREE REPORTED ON LINE AT 412 CLAYTON / ALSO AT 2020 MARKHAM..NEED FLAGGERS AND TREE CREW ON 417 CLAYTON RD Simmons, Michael (919) 437-9709 @7:58 called flaggers at 802***circuit out see 11197960 tree fell taking down primary lines breaking pole. crew cut jumpers to isolate see 11198066 and got circuit back on ...after repairs crew dropped circuit again see 11198298 to make jumpers back. ~~~ 4/29/2019 ¦ rlw2159 ¦ Investigative Action
Veg | Chapel Hill rlw2159 | EASTGATE RET - 19021208 | 4/28/2019 05:04 | 4/28/2019 05:50 | 11198298 | S-CKT - ABC Size: Class 1 FID: 38359209 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | P1 Pole, Creosote | OA Oak | 25 | P3 R Scheduled Outage | 03 Wind | 774 | 800 | 46 | 412 CLAYTON RD | DROPPED CIRCUIT TO MAKE UP JUMPERS - SEE EV11198066 | rlw2159-windy condition...large co dominate oak approximately 3" round at base, 25' feet from center line fell due to wet area and defective base-- CKT LOCKOUT/FMAG 2968 A C TRIP 50/MOST LIKELY FAULT LOCATION NEAR FACID 38587733 OLD OXFORD AT MARKHAM DR - TREE REPORTED ON LINE AT 412 CLAYTON / ALSO AT 2020 MARKHAM..NEED FLAGGERS AND TREE CREW ON 417 CLAYTON RD Simmons, Michael (919) 437-9709 @7:58 called flaggers at 802***circuit out see 11197960 tree fell taking down primary lines breaking pole. crew cut jumpers to isolate see 11198066 and got circuit back on ...after repairs crew dropped circuit again see 11198298 to make jumpers back. ~~~ 4/29/2019 ¦ rlw2159 ¦ Investigative Action
Veg | Sanford i25781 | JONESBORO 230KV - BROADWAY 24KV | 5/3/2019 10:57 | 5/3/2019 11:53 | 5042973 | RECLOSER - ABC FID: 17GW43_104175200 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin | 29 Conductor, bare | PN R Surge Protection Device |  | F2 Forced Outage | 00 Calm | 1,133 | 1147 | 56 | 6557AC | Tree/Vegetatn Limb Fell from Inside Right of Way None limb at 6557AC | JWW// On 5/3/19 at 10:57am a small limb fell across all 3 phases at 6557AC locking out G&W 17GW43 causing 1133 customers to lose power. When the line tech arrived he knocked off limb and had DCC energize G&W at 11:53 restoring power to all customers. No damage done to conductor. ~~~ 5/16/2019 ¦ i25781 ¦ Investigative Action
Veg | Garner c72037 | AUBURN 230KV - ROCK QUARRY ROAD 23KV | 5/4/2019 20:39 | 5/4/2019 21:38 | 5043626 | RECLOSER - XYZ FID: EC15BJ_104362554 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DC Internal stem decay | NA | OA Oak | 15 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,324 | 2690 | 59 | ED07BJ | Tree/Vegetatn Limb Fell from Inside Right of Way None tree limb at ED07BJ | MHS- added outage customer count from outage 5043620 which is part of this outage just B phase that was made a separate outage from A&C phase. A 6 " in DIA. defective white oak branch broke out of tree about 45' above ground level, falling across all 3 phases of primary locking out Recloser EC15BJ. Crew cleared limb and had DCC re-energize the recloser. ~~~ 5/10/2019 ¦ c72037 ¦ Investigative Action
Veg | Chatham County C80721 | BYNUM 230KV - BYNUM 23KV | 5/13/2019 10:05 | 5/13/2019 11:19 | 5046111-1 | SWITCH - ABC FID: N940AF_24909 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | LR Tree limb, dead, overhang | 39 Repaired Overhead Conductor | 29 Conductor, bare | UN Unknown Species | 0 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,698 | 4287 | 74 | aarias// PMX22 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE | aarias// storm in area. Dead overhang limb of unknown species made contact with 3-ph primary and burned down A-ph of 477 wire before recloser operated. Damage isolated and backfed from the Chapel Hill 24KV feeder at switch N193AF until repairs were completed. WO 32901778 created for I&C tech to check recloser settings (TNorris/TMedford) verified settings ok, Recloser operated properly - B&C phases operated a couple of times prior to lock out, Remote Open Command sent to open A phase. ~~~ 5/21/2019 ¦ C80721 ¦ Work Order(s) Generated
Veg | Garner c72037 | WAKE TECH 230KV - BANKS 24KV | 5/13/2019 13:38 | 5/13/2019 15:53 | 5046340 | RECLOSER - ABC FID: 10TC62_113087540 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | NA | SZ Sweet Gum | 60 | F2 Forced Outage | 04 Wind, Rain and Lightning | 556 | 1824 | 135 | Node~26096690 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree cleared. tree | MHS- Crew found a 18" in DIA. defective sweet gum tree had fallen across the road and all 3 phases of primary, locking out recloser 10TC62. Crew cleared tree and had DCC re-energize the recloser. ~~~ 5/20/2019 ¦ c72037 ¦ Investigative Action
Veg | Asheboro i25781 | ASHEBORO EAST 115KV - MEADOWBROOK ROAD 23KV | 5/14/2019 09:06 | 5/14/2019 09:58 | 5046674 | OCB - ABC FID: T0960B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | 29 Conductor, bare | OA Oak | 23 | F2 Forced Outage | 03 Wind | 1,205 | 1201 | 52 | Load~F885AD | Tree/Vegetatn Tree outside Right of Way (Fall/Lean On Primary) None Tree on line. | JWW// On 5/14/19 at 09:06am a tree outside of the right of way broke 3' from the ground and fell in all 3 phases locking out the Meadowbrook FDR and causing 1205 customers to lose power. When service tech arrived he cut tree off of primary and had DCC energize FDR at 09:58am restoring power to all 1205 customers. It was very windy that day and no damage was done to conductor. ~~~ 5/16/2019 ¦ i25781 ¦ Investigative Action
Veg | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 5/26/2019 12:44 | 5/26/2019 12:51 | 5050110-1 | RECLOSER - ABC FID: BR21BJ_104162335 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | NA | HK Hickory | 75 | P4 Crew Initiated Outage | 00 Calm | 1,366 | 2735 | 7 | OL67 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON 3 PHASES AT 0L67 | MHS-a 14" in DIA. defective hickory tree fell 75' from C/L onto all 3 phases of the Woodland road feeder. Service tech. had DCC open recloser BR21BJ to cut tree in the clear. After service tech cleared tree he had DCC re-energize the recloser ~~~ 6/12/2019 (17 days) ¦ c72037 ¦ Investigative Action
Veg | Garner c72037 | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 5/31/2019 18:32 | 5/31/2019 20:05 | 5052335-1 | RECLOSER - ABC FID: DG24BJ_104176315 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect | NA | 28 Other Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,755 | 2868 | 93 | Line~DZ12BJ_DZ13BJ | Tree/Vegetatn Tree/Limb Growth None tree limbs btw DZ13BJ and DZ24BJ | MHS- Crew rode out line and found several spots where trees were burning into the primary crews had DCC open up A phase (outage 5052531)to trim trees, crew than had DCC re-energize re-closer which held for about a min. than went back out B&C phases (outage 5052567) crew did more trimming than had DCC re-energize recloser and it held this time ~~~ 6/5/2019 ¦ c72037 ¦ Investigative Action
Veg | Durham dlm4375 | POPE ROAD - 14082410 | 5/31/2019 18:34 | 5/31/2019 21:47 | 11232403 | S-RCL - ABC Size: 800 VPTT FID: 410892867 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect |  | OW Oak, willow | 0 | F2 Forced Outage | 04 Wind, Rain and Lightning | 640 | 2077 | 193 | Picket Rd and Ashlan Dr | RCL lockout B C FAULT FMAG 3163...FID 410892867 also locked out and rolled under this RCL. SHT74 disabled | dlm4375 storm in area..had Rec device 410892867 see 11232403 on Petty Rd off and Rec device 410781226 see 11232151 at Westgate Dr and Chapel hill Blvd off..found a willow oak limbs over grown into the 3phase oh Primary which burned in the clear, located on Picket Rd at Ashland Dr. The lineman energized Rec device 410781226 at Westgate Dr and Chapel hill Blvd and it held. Then the lineman went to energize Rec device 410892687 on Petty Rd and it by passed the upstream Rec device 410781226 at Westgate Dr and Chapel hill Blvd and rec device 410841375 on Lyckan Parkway and the rec device 410862847 corner of Garrett Rd and Durham Chapel Hill Blvd and took out Pope Rd 2410 circuit see 11232442. This is a self healing team that is disabled at this time and under review with Reid Daniels. Sent email to Reid to see status of the self healing team and also this circuit is to be trimmed this year. Starting next 2 weeks. see attached pictures and string to emails and the new online that is proposed. ~~~ 6/4/2019 ¦ dlm4375 ¦ Investigative Action
Veg | Durham i40607 | GARRETT RD - 14202413 | 5/31/2019 18:36 | 5/31/2019 21:13 | 11232185 | S-RCL - ABC Size: 560 WVE FID: 39009202 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | 26 Vines | 16 Closed Recl or Sectionalizer | NA | 28 Other Species | 0 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,559 | 5342 | 157 | FID-38526567-DIP FOR PARSONS CHASE. | RECLOSER LOCKOUT TARGET AG FMAG COULD NOT PULL FROM RELAY...no problem found, tried recloser and it held...kwb | rlw2159--VINES ON OUTAGE ID# 11232606 CAUSED THE BLINK(11232172) ON THIS RECLOSER AND THE RECLOSER TO LOCK OUT. CREW DIDN'T SEE THIS AT THIS TIME. ~~~ 6/4/2019 ¦ i40607 ¦ Investigative Action
Veg | Garner c72037 | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 5/31/2019 19:56 | 5/31/2019 20:05 | 5052531 | RECLOSER - A FID: DG24BJ_104176315 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LX Trees, overgrown primary | DN No apparent defect | NA | 28 Other Species |  | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 672 | 2868 | 9 | DZ13BJ | Missing Missing Missing | MHS- Crew rode out line and found several spots where trees were burning into the primary crews had DCC open up A phase (outage 5052531)to trim trees, crew than had DCC re-energize re-closer which held for about a min. than went back out B&C phases (outage 5052567) crew did more trimming than had DCC re-energize recloser and it held this time ~~~ 6/5/2019 ¦ c72037 ¦ Investigative Action
Veg | Cary c72037 | RALEIGH OAKDALE 230KV - ROYLENE 23KV | 5/31/2019 20:04 | 5/31/2019 22:02 | 5052557 | OCB - ABC FID: T5136B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | NA | OA Oak | 20 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,793 | 2780 | 118 | GM67K | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Tree on a three phases at GM65K | MHS- crew found a 8" in DIA. defective oak tree had broke about 45' from ground level falling across all 3 phases of the ROYLENE feeder locking out the FCB. the crew cleared tree and had DCC close the FCB back in ~~~ 6/12/2019 ¦ c72037 ¦ Investigative Action
Veg | Durham dlm4375 | POPE ROAD - 14082410 | 5/31/2019 20:04 | 5/31/2019 21:47 | 11232442 | S-CKT - ABC Size: Class 2 FID: 38356089 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | LX Trees, overgrown primary | DN No apparent defect |  | OW Oak, willow | 0 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,444 | 2077 | 103 | Picket Rd and Ashland Dr | lockout...ABC targets...637 FMAG... | dlm4375 storm in area..had Rec device 410892867 see 11232403 on Petty Rd off and Rec device 410781226 see 11232151 at Westgate Dr and Chapel hill Blvd off..found a willow oak limbs over grown into the 3phase oh Primary which burned in the clear, located on Picket Rd at Ashland Dr. The lineman energized Rec device 410781226 at Westgate Dr and Chapel hill Blvd and it held. Then the lineman went to energize Rec device 410892687 on Petty Rd and it by passed the upstream Rec device 410781226 at Westgate Dr and Chapel hill Blvd and rec device 410841375 on Lyckan Parkway and the rec device 410862847 corner of Garrett Rd and Durham Chapel Hill Blvd and took out Pope Rd 2410 circuit see 11232442. This is a self healing team that is disabled at this time and under review with Reid Daniels. Sent email to Reid to see status of the self healing team and also this circuit is to be trimmed this year. Starting next 2 weeks. see attached pictures and string to emails and the new online that is proposed. ~~~ 6/4/2019 ¦ dlm4375 ¦ Investigative Action
Veg | Garner c72037 | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 5/31/2019 20:05 | 5/31/2019 20:31 | 5052567 | RECLOSER - BC FID: DG24BJ_104176315 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LX Trees, overgrown primary | DN No apparent defect | NA | 28 Other Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,830 | 2868 | 26 | DZ13BJ | Missing Missing Missing | MHS- Crew rode out line and found several spots where trees were burning into the primary crews had DCC open up A phase (outage 5052531)to trim trees, crew than had DCC re-energize re-closer which held for about a min. than went back out B&C phases (outage 5052567) crew did more trimming than had DCC re-energize recloser and it held this time ~~~ 6/5/2019 ¦ c72037 ¦ Investigative Action
Veg | Cary c72037 | RALEIGH SOUTH 115KV - LAKE DAM 23KV | 5/31/2019 20:26 | 5/31/2019 22:05 | 5052659-1 | RECLOSER - XY FID: 17H197_104157003 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | NA | PP Yellow Poplar (tulip) | 45 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,200 | 2974 | 99 | LQ44K | Tree/Vegetatn Limb Fell from Outside Right of Way None limb fell on all three phases at lq44k | MHS- Crew had outage on re-closer 17H197 B & C phases crew rode out line and found a 12" in DIA. defective popular tree at LQ44K had fell across all 3 phases. crew had DCC then open up A phase (outage 5052662) for safety reasons, crew cut tree in clear than had DCC re-energize line ~~~ 6/5/2019 ¦ c72037 ¦ Investigative Action
Veg | Cary c72037 | RALEIGH SOUTH 115KV - LAKE DAM 23KV | 5/31/2019 20:30 | 5/31/2019 22:05 | 5052662 | RECLOSER - A FID: 17H197_104157003 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | NA | PP Yellow Poplar (tulip) | 45 | F2 Forced Outage | 04 Wind, Rain and Lightning | 501 | 2974 | 95 | LQ44K | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | MHS- Crew had outage on re-closer 17H197 B & C phases crew rode out line and found a 12" in DIA. defective popular tree at LQ44K had fell across all 3 phases. crew had DCC then open up A phase (outage 5052662) for safety reasons, crew cut tree in clear than had DCC re-energize line ~~~ 6/5/2019 ¦ c72037 ¦ Investigative Action
Veg | Chatham County C80721 | BYNUM 230KV - BYNUM 23KV | 5/31/2019 22:39 | 5/31/2019 23:33 | 5052912 | OCB - ABC FID: T1025B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | 37 Removed Limb or Tree From Lin | NA | PP Yellow Poplar (tulip) | 16 | F2 Forced Outage | 04 Wind, Rain and Lightning | 4,224 | 4287 | 54 | BV23AF | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | LWB, During strong Thunderstorm top wrenched out of Tulip popular Tree, 70+ feet tall, 30 +" around. Tree is 16' outside of ROW, side trimmed, along Karen Calhoun Road. ROW is trimmed well/mowed. No defects noticed in tree. BV23AF ~~~ 6/3/2019 ¦ C80721 ¦ No Action Required
Veg | Garner c72037 | GARNER TRYON HILLS 115KV - YEARGAN ROAD 24KV | 6/1/2019 08:17 | 6/1/2019 09:42 | 5053194-1 | RECLOSER - AB FID: 109879_104191792 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DC Internal stem decay | NA | OW Oak, willow | 5 | F2 Forced Outage | 00 Calm | 1,083 | 1928 | 85 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None tree limb cleared and restored to normal | MHS-crew arrivied to find a defective 6" in DIA. oak limb had broke off about 30' above ground level and laid over on primary opening up A and B phases crew opened up sectionalizers at FN25BJ. then had DCC close the re-closer back in getting all but 180 customers back on ~~~ 6/5/2019 ¦ c72037 ¦ Investigative Action
Veg | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 6/5/2019 16:28 | 6/5/2019 17:36 | 5055071-1 | OCB - ABC FID: T4720B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | NA | SZ Sweet Gum | 90 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,235 | 2735 | 68 | 2X430 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE AT 2X430 Tree on line at 2X430, opened ABS T490BJ at 5:36 energized breaker for partial restore. kv | MHS-Crew found a 20" in DIA. defective Sweet gum had uprooted out of a shallow stream falling onto all 3 phases of the woodland road feeder locking out the FCB. the crew than opened up ABS T490BJ getting 1734 customers back on. the crew then cleared the tree at 2X430 and then closed the ABS back in. ~~~ 6/12/2019 ¦ c72037 ¦ Investigative Action
Veg | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 6/5/2019 16:28 | 6/5/2019 19:12 | 5055071-2 | SWITCH - ABC FID: T490BJ_2842178 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | NA | SZ Sweet Gum | 90 | F2 Forced Outage | 04 Wind, Rain and Lightning | 501 | 2735 | 164 | 2X430 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE AT 2X430 Tree on line at 2X430, opened ABS T490BJ at 5:36 energized breaker for partial restore. kv | MHS-Crew found a 20" in DIA. defective Sweet gum had uprooted out of a shallow stream falling onto all 3 phases of the woodland road feeder locking out the FCB. the crew than opened up ABS T490BJ getting 1734 customers back on. the crew then cleared the tree at 2X430 and then closed the ABS back in. ~~~ 6/12/2019 ¦ c72037 ¦ Investigative Action
Veg | Durham rlw2159 | POPE ROAD - 14082403 | 6/7/2019 20:36 | 6/7/2019 22:35 | 11239951 | S-RCL - ABC Size: 800 VPTT FID: 404709669 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | 27 Other/See Notes | 29 Conductor, bare | OA Oak | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,907 | 3227 | 119 | erwin rd and timberly in field | CMPL 2019-06-07 22:35:00 by WJAMES RMK: RECL LOCKOUT A G FAULT CAJ3396 SHT 74 ALREADY DISABLED | dlm4375 storm in area...self healing is disabled... had a tree limb laying on neutral and bottom phase overhead primary on vertical construction...located at ewrin Rd and timberly....RLW2159-COULDN'T PICTURES OF DEAD OAK TREE DUE TO A BARB WIRE FENCE AND POISON OAK. THE TREE IS IN A PASTURE. THIS CIRCUIT IS PRESENTLY BEING TRIMMED. ~~~ 6/11/2019 ¦ rlw2159 ¦ Investigative Action
Veg | Raleigh DFontan | PINE LAKE 230KV - FOX ROAD 24KV | 6/8/2019 01:20 | 6/8/2019 02:07 | 5056252-1 | OCB - ABC FID: T5108B14 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | NA | AS Ash |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,878 | 1904 | 47 | Line~BR84BK_BR85BK_1184074 | Tree/Vegetatn Tree/Limb Growth None BRANCH ACROSS ALL THREE PHASES | Fontana 6/10/19 - A 1" diameter by ~6' long dead limb from a 1' diameter from ~70' tall ash tree located ~23' from the feeder center line broke and got caught up in the primary between poles BR84BK and BR85BK. Unable to determine where limb broke off from tree. C&M responder knocked the limb down and had DCC remotely energize feeder. No Damage. ~~~ 6/10/2019 ¦ DFontan ¦ Investigative Action
Veg | Sanford i25781 | SANFORD HORNER BLVD. 230KV - CHATHAM STREET 23KV | 6/9/2019 06:30 | 6/9/2019 07:21 | 5056987 | OCB - ABC FID: T2440B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | 29 Conductor, bare | PT PINE | 17 | F2 Forced Outage | 00 Calm | 1,948 | 1948 | 51 | 6848AC | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None LIMB ON LINE AT 6848AC | JWW// On 6/9/19 at 06:30 a pine limb fell on three phase locking out the Chatham ST. FDR. When service tech arrived he found that the limb fell across the three phase and it had cleared itself so he had DCC energize the FCB restoring power to all 1948 customers at 07:21. No damage was done to conductor. ~~~ 6/13/2019 ¦ i25781 ¦ Investigative Action
Veg | Sanford i25781 | SANFORD HORNER BLVD. 230KV - CHATHAM STREET 23KV | 6/11/2019 08:53 | 6/11/2019 09:01 | 5058001 | OCB - ABC FID: T2440B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | 29 Conductor, bare | OA Oak |  | P4 Crew Initiated Outage | 00 Calm | 1,948 | 1948 | 8 | 6858AC | Tree/Vegetatn Limb Fell from Inside Right of Way None TREE LIMB ON LINE 6858AC | JWW// On 6/11/19 a customer called in a limb burning on the primary. When the service tech arrived there was a small limb laying on 2 of the phases burning so he had DCC de-energize the FCB and removed the limb then had DCC energize the FCB. The outage lasted 7 minutes. Could not find where the limb fell from. No damage was done to the conductor. ~~~ 6/18/2019 ¦ i25781 ¦ Investigative Action
Veg | Durham rlw2159 | ELLIS RD RET - 14192413 | 6/19/2019 03:38 | 6/19/2019 04:33 | 11254436 | S-CKT - ABC Size: Class EX FID: 38375361 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | NA | OA Oak |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 775 | 774 | 55 | 4213 S Alston Ave | CIRCUIT LOCKOUT. rESET ocb cause limb across two phases at 4213 S Alston Ave was cause | rlw2159-storm in area-CIRCUIT LOCKOUT. rESET ocb cause limb across two phases at 4213 S Alston Ave was cause--blink ticket# 11254435 is associated with this outage. Couldn't tell exactly where the limb came from. ~~~ 6/20/2019 ¦ rlw2159 ¦ Investigative Action
Veg - MED | Durham omshistproc | GARRETT RD - 14202411 | 6/20/2019 15:35 | 6/20/2019 16:56 | 11257378 | S-CKT - ABC Size: Class 1A FID: 38355885 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | LH Tree limb, overhang | 14 Closed Breaker | S9 Breaker |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,891 | 2920 | 81 | 6514 garrett rd | CMPL 2019-06-20 17:07:00 by JAU4299 RMK: CKT LOCKOUT pin oak limb accross 3 phase @ 6514 garrett rd | pin oak limb accross 3 phase... NO OUTAGE REVIEW INFO
Veg - MED | Chapel Hill omshistproc | EASTGATE RET - 19021204 | 6/20/2019 15:36 | 6/20/2019 18:39 | 11257425 | S-CKT - ABC Size: Class 1 FID: 38358873 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | 03 Tree (Vegetation) | 27 Other/See Notes | 29 Conductor, bare |  |  | F2 Forced Outage |  | 1,824 | 1963 | 183 | plant rd and e franklin st | CMPL 2019-06-20 18:44:00 by BJACOBY RMK: TREE/POLE/LINES DOWN 101 PLANT RD LOCKOUT BG FAULT FMAG 2543 | tree on plant rd broke pole and cause tap wires to break. the unfused three phase on plant rd is what took the circuit out... NO OUTAGE REVIEW INFO
Veg - MED | Chapel Hill omshistproc | GREY - 19091207 | 6/20/2019 15:52 | 6/20/2019 17:14 | 11257577 | S-RCL - ABC Size: 800 VPST FID: 39005248 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 16 Closed Recl or Sectionalizer |  |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 819 | 1886 | 82 | WHIPPORWHILL AND FARRIGNTON | BC LOCKOUT FMAG 1921 / TL524 TEER REMOVED TREE AT WHIPPORWHILL AND FARRINGTON | ... NO OUTAGE REVIEW INFO
Veg - MED | Chatham County rlw2159 | PITTSBORO 230KV - NORTHWOOD 23KV | 6/20/2019 16:05 | 6/20/2019 17:09 | 5061458 | OCB - ABC FID: T2250B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  | OA Oak | 25 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,209 | 2225 | 64 | AF92AF | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree outside r-o-w at AF92AF tree outside r-o-w at AF92AF | rlw2159--3 small oak trees from about 25' from center line fell on 3 phase primary-Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree outside r-o-w at AF92AF tree outside r-o-w at AF92AF ~~~ 7/1/2019 ¦ rlw2159 ¦ Investigative Action
Veg - MED | Garner omshistproc | GARNER I-40 230KV - BARWELL ROAD 24KV | 6/20/2019 16:08 | 6/20/2019 18:19 | 5061484-1 | SWITCH - ABC FID: 154M51_103140351 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,014 | 2365 | 131 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Repairs made. | ... NO OUTAGE REVIEW INFO
Veg - MED | Raleigh omshistproc | PINE LAKE 230KV - OAK FOREST ROAD 24KV | 6/20/2019 16:48 | 6/20/2019 18:52 | 5061751-2 | OCB - ABC FID: T5108B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,012 | 2484 | 124 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree at bl32bk | ... NO OUTAGE REVIEW INFO
Veg - MED | Asheboro omshistproc | RAMSEUR 115KV - COLERIDGE 24KV | 6/20/2019 17:04 | 6/20/2019 19:20 | 5061875 | RECLOSER - ABC FID: 8LN91_2300560 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 571 | 1462 | 135 | Recloser~8LN91_2300560 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree on primary @ 50U42. trees on primary lines/trees on primary lines/trees on primary | ... NO OUTAGE REVIEW INFO
Veg - MED | Cary omshistproc | NEW HILL 230KV - NEW HILL 23KV | 6/20/2019 17:51 | 6/20/2019 19:31 | 5062293 | OCB - ABC FID: T5911B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,220 | 1223 | 101 | Switch~T5911B01 | Tree/Vegetatn Limb Fell from Outside Right of Way None Tree fell from outside of right of way at 8262K. | ... NO OUTAGE REVIEW INFO
Veg - MED | Garner omshistproc | GARNER WHITE OAK 230KV - WHITE OAK 24KV | 6/20/2019 18:14 | 6/20/2019 19:33 | 5062460-1 | OCB - ABC FID: T4730B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 02 Rain | 1,865 | 1912 | 78 | Line~X589_X591_1166162 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Isolated at X589 and re-energized the feeder. RESTORED UP TO X589 | ... NO OUTAGE REVIEW INFO
Veg | Asheboro i14740 | ASHEBORO WEST 115KV - UWHARRIE STREET 23KV | 6/24/2019 23:38 | 6/25/2019 00:18 | 5065926 | RECLOSER - BC FID: 128943_104203154 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect | NA | BB Bamboo | 7 | F2 Forced Outage | 04 Wind, Rain and Lightning | 922 | 2805 | 40 | Line~9570AD-94G19 | Tree/Vegetatn Tree/Limb Growth None BAMBOO | A patch of bamboo, 7' from centerline, between 9570AD and 94G19, grew into 3 phase line causing the outage. The bamboo was cut and the ROW cleared for any other potential issues. BDH ~~~ 6/25/2019 ¦ i14740 ¦ Investigative Action
Veg | Durham rlw2159 | ENO - 14102402 | 6/28/2019 16:34 | 6/28/2019 22:14 | 11273158 | P3OH - ABC Size: JUMPERS FID: 34182433 | 09 Jumper/wire cut/open | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | D2 Dead | 29 Conductor, bare | PT PINE | 16 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,992 | 2020 | 340 | 5401 groucho rd. | CMPL 2019-06-28 22:16:00 by SJLINDE RMK: CIRCUIT LOCKOUT/FAULT CLOSE TO STATION - STATION TECH AWARE - TREE TOOK LINE DWN 5401 GROUCHO RD - BRKN CROSS ARMS ...tecjh call S Lindermuth (919-723-7866) 2 SPANS OF PRIMARY NEUTRAL DOWN AND BROKEN CROSS ARM | rlw2159--partially dead fork of a pine tree broke of approximately 16' from center line-cut jumper at FID# 86400349 to get ckt back on-replaced crossarm, 50' of 336 OH wire, 2 insualtor, 1 pole top, 1 24kv fault tamer and cutout, had to drop circuit again to make jumpers up at ID 86400349. Related tickets-11272984-blink, 11272985-circuit, 11273244-circuit opened to make up jumpers ~~~ 7/2/2019 ¦ rlw2159 ¦ Investigative Action
Veg | Garner e68825 | RALEIGH WORTHDALE 230KV - GLENBROOK 23KV | 6/30/2019 17:33 | 6/30/2019 20:10 | 5067778 | OCB - ABC FID: T5168B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | AS Ash | 0 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,592 | 1591 | 157 | RDM15-AH31BJ | Tree/Vegetatn Limb Fell from Outside Right of Way None | PEEL 7/1/19: During a T-Storm a 4" dia. x ~20' long live limb broke off the overhang of a 2' dia. x ~75' tall Carolina Ash, 25' off of the line CL, and fell onto the double circuit of the Rose Lane and Glennbrook feeders in span RDM15-AH31BJ, and locked out both feeders. Responding crew removed the tree limb from the lines , and had DCC remotely close both FCBs to restore service to both feeders. No Damage. ~~~ 7/1/2019 ¦ e68825 ¦ Investigative Action
Veg | Garner e68825 | RALEIGH WORTHDALE 230KV - ROSE LANE 23KV | 6/30/2019 17:33 | 6/30/2019 20:07 | 5067775-2 | OCB - ABC FID: T5168B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | AS Ash | 0 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,439 | 1833 | 154 | Line~RDM15_AH31BJ_1165842 | Tree/Vegetatn Limb Fell from Inside Right of Way None tree fell btw AH31BJ and RDM15 | PEEL 7/1/19: During a T-Storm a 4" dia. x ~20' long live limb broke off the overhang of a 2' dia. x ~75' tall Carolina Ash, 25' off of the line CL, and fell onto the double circuit of the Rose Lane and Glennbrook feeders in span RDM15-AH31BJ, and locked out both feeders. Responding crew removed the tree limb from the lines , and had DCC remotely close both FCBs to restore service to both feeders. No Damage. ~~~ 7/1/2019 ¦ e68825 ¦ Investigative Action
Veg | Garner c72037 | CLAYTON 115KV - TV 24KV | 6/30/2019 17:51 | 6/30/2019 19:43 | 5067808 | RECLOSER - ABC FID: ND17BJ_1624697 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | TF Tree fails, defective | DR Roots rotten/defective | P2 Pole, CCA | OA Oak | 24 | F2 Forced Outage | 17 Wind and Rain | 526 | 1960 | 112 | DH71BJ | Overhead Fac Pole Failure Broke (Other...Comments) pole broke opened SBD @ nd17bj OPEN SOLID BLADES AT DH37BJ | MHS- A defective 20" in DIA. oak tree fell across all 3 phases of primary breaking pole DH37BJ about 12' from ground level, crew opened up solid blades at DH37BJ and closed oil reclosers at ND17BJ to get all but 77 customers back on another outage was made for the 77 customers outage # 5067870 ~~~ 7/11/2019 ¦ c72037 ¦ Investigative Action
Dist | Asheboro i25781 | ASHEBORO EAST 115KV - ASHEBORO EAST HIGHWAY 64 23KV | 4/2/2019 13:24 | 4/2/2019 14:56 | 5027986 | RECLOSER - ABC FID: L129AD_103522824 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA | NA R |  | F2 Forced Outage | 00 Calm | 685 | 1751 | 92 | L174AD | Human Interf OH - Vehicle None Truck hit pole, broke pole off at ground , neutral broke on ground DIS# L174AD Truck hit pole, broke pole off at ground , neutral broke on ground DIS# L174AD | JWW// On 4/2/19 at 01:24pm a truck ran off the road and hit a 3 phase pole at dis# L174AD locking out G&W and causing 685 customers to loose power. Crew replaced pole then had DCC energize the G&W at 02:56pm restoring power to all 685 customers. ~~~ 4/9/2019 ¦ i25781 ¦ Investigative Action
Dist | Durham dlm4375 | FAIRNTOSH - 14142410 | 4/7/2019 09:04 | 4/7/2019 09:52 | 11165528 | S-CKT - ABC Size: Class 2 FID: 38356473 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | 08 Error, Duke | MP Porcelain | SR Software | C5 Chance (A B) |  | F2 Forced Outage | 00 Calm | 3,172 | 3589 | 48 | BURNT POLE TOP IN FRONT OF 1602 HAMLIN RD | LOCK OUT ON WEAVER 2412 & FAIRNTOSH 2410. BURNT POLE TOP IN FRONT OF 1602 HAMLIN RD. OPENED RECLOSER 39005599 TO ISOLATE FAULT AND CLOSE 2410 BREAKER. BRIAN JACOBY & ALEX RUDD....dlm4375 crew replaced 1-45/4 pole 1-10' and 1-8' x arm, 6 insulators and 1 25kv switch..I sent transmission tech to substation to get events to see if can find fault and also the tech turned in order because the phone in substation is not working..***update on fairntosh 2410 DPAC conducted a coordination study and found that there wasn't a desired amount of margin between the CB and Rec. So we had to modify the setting on the rec.*** | dlm4375 had a double circuit pole catch on fire located in front of 1602 Hamlin Rd due to a bad slick top cutout that broke down and caught pole on fire. Double circuits involved: fairntosh 2410 which locked out recl facid 39005599 see 11165552 other circuit involved Weaver 2412 circuit locked out see 11165527 only 1 customer off. we also had the cir on Fairntosh 2410 to lock out see 11165528 at the same time as the recl on fairntosh locked out unfortunately Farintosh circuit is not in ESNET and you can not dail in on Procum to get the fault location of where to invest midspan fault or what. Crew rode cir got circuit back on see 11165528 then Crew opened some disc facid 86404552 see 11165582 on fairntosh 2410 to isolate to get some cust back on. email to GIS to fix GIS becuase disconnects are showing on Weaver 2412 but not on Fairntosh 2410 and the disc are in the field on the double circuit pole for both circuits. crew opened fairntosh 2410 rec see 11165664 to close in rec.*update on cir fairn 2410 see email ~~~ 4/9/2019 ¦ dlm4375 ¦ Investigative Action
Dist | Sanford i25781 | SANFORD GARDEN STREET - SANFORD GARDEN STREET HOSPITAL 23KV | 4/12/2019 17:16 | 4/12/2019 18:45 | 5032596 | RECLOSER - AB FID: 0021AC_2485393 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | HZ Cause undetermined | 24 N/A | 00 R Sectionalizer | NA R |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 620 | 1391 | 89 | Recloser~0021AC_2485393 | Service tech did not find anything. | JWW// On 4/12/19 during a strong thunderstorm G&W 0021AC locked out. When the service tech arrived he could not find anything so he had DCC energize the G&W and it held. I looked up faults in FMS and tried to find where a limb could have fell on the 3 phase. Never did find anything. ~~~ 4/25/2019 ¦ i25781 ¦ Investigative Action
Dist | Garner c72037 | DUNCAN 230KV - DUNCAN 24KV | 4/13/2019 01:46 | 4/13/2019 02:44 | 5032849 | RECLOSER - ABC FID: J805BH_103783585 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | MS Steel | G1 Guywire | NA R |  | F2 Forced Outage | 02 Rain | 733 | 2626 | 58 | 7XP07 | Human Interf OH - Vehicle None car hit pole car hit pole | MHS-car left road and hit the down guys causing them to break and get wrapped up in to the primary, locking out recloser JB05BH. crew cleared guys from primary and had DCC close the recloser back in. ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Dist | Sanford i25781 | BEAR BRANCH 230KV - BENHAVEN 24KV | 4/14/2019 19:00 | 4/14/2019 20:45 | 5033496-2 | RECLOSER - ABC FID: 10KJ15_112670000 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA | NA R |  | F2 Forced Outage | 00 Calm | 537 | 1572 | 105 | 1ATT82 | Human Interf OH - Vehicle None | JWW// On 4/14/19 at 19:00 a car broke a pole at DIS#1ATT82 causing 586 customers to lose power. When service tech arrived he opened 3 solid blade disconnects at 15FD04 and had DCC back feed 49 customers using G&W U8S78. After pole was replaced DCC energized G&W 10KJ15 at 20:45restoring power to the remaining 537 customers. Crew then switched everything back to normal. ~~~ 4/25/2019 ¦ i25781 ¦ Investigative Action
Dist - MED | Cary C80721 | CARY 230KV - WEST CHATHAM STREET 23KV | 4/15/2019 03:38 | 4/15/2019 06:49 | 5033891 | OCB - ABC FID: T4600B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | 21 Slack Conductors | 39 Repaired Overhead Conductor | NA | UN Unknown Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 3,411 | 3395 | 191 | aarias// 8391K | Overhead Fac Overhead Primary Failure (No Tree Involved) Slack Conductor/Sag/Improper Roll | aarias// storm in area. Insulator failed on the Cary 23KV feeder. Crews cleared it and transferred the load to W Chatham St 23KV. Replaced insulators and cutouts on the Cary feeder and resagged primary on the W Chatham St feeder 5033891- W Chatham St 23KV outage. 5033727- Cary 23KV outage -Cyme for customer count. Accuracy reviewed with BLittle ~~~ 4/16/2019 ¦ C80721 ¦ Investigative Action
Dist - MED | Cary C80721 | CARY 230KV - CARY 23KV | 4/15/2019 05:47 | 4/15/2019 06:50 | 5034021 | OCB - ABC FID: T4600B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 46 Replaced Insulator | 38 Insulator | UN Unknown Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 802 | 1574 | 63 | aarias// 8391K | Overhead Fac Overhead Insulator Failure Other Post Insulator Broke/Cracked replaced insulators and cutouts | aarias// storm in area. Second damaged insulator failed (see tkt 5033727). Feeder was clear at the time of outage and load had been transferred to West Chatham St 23KV. See outages. Cust count reviewed for accuracy in Cyme/BL assisted 5033891- W Chatham St 23KV 5033727- Cary 23KV ~~~ 4/16/2019 ¦ C80721 ¦ Investigative Action
Dist - MED | Cary AArias | CARY PINEY PLAINS 230KV - SWIFT CREEK 24KV | 4/15/2019 05:55 | 4/15/2019 07:37 | 5034028-3 | RECLOSER - ABC FID: 1CEQ10_115206336 | 02 Line Recloser | UG Distribution Line Underground | 20 Equipment failure | DC Insulation Failure | 56 Sectionalized/Restored Servic | U1 Cable, UG, Primary | UN Unknown Species |  | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 529 | 1457 | 102 | Line~13XG94_CAX48_2787417 | Undergrnd Fac Underground Primary Failure Cable Failed BAD UG 750 between H424K AND CAX48 | aarias// storm in area. 750 UG primary failed. Normal feed comes out of Roylene 23KV, was backfed from Swift Creek to isolate outage at Roylene (see tkt 5033619) 5034028-1 feeder outage 5034028-2 opened feeder tie switch at H392K 5034028-3 opened recloser at 1CEQ10 ~~~ 4/17/2019 ¦ AArias ¦ Investigative Action
Dist - MED | Cary AArias | CARY PINEY PLAINS 230KV - SWIFT CREEK 24KV | 4/15/2019 05:55 | 4/15/2019 07:35 | 5034028-2 | SWITCH - ABC FID: H392K_2733658 | 08 Disconnect | UG Distribution Line Underground | 20 Equipment failure | DC Insulation Failure | 56 Sectionalized/Restored Servic | U1 Cable, UG, Primary | UN Unknown Species |  | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 2,058 | 1457 | 100 | Line~13XG94_CAX48_2787417 | Undergrnd Fac Underground Primary Failure Cable Failed BAD UG 750 between H424K AND CAX48 | aarias// storm in area. 750 UG primary failed. Normal feed comes out of Roylene 23KV, was backfed from Swift Creek to isolate outage at Roylene (see tkt 5033619). No pictures 5034028-1 feeder outage 5034028-2 opened feeder tie switch at H392K 5034028-3 opened recloser at 1CEQ10 ~~~ 4/17/2019 ¦ AArias ¦ Investigative Action
Dist - MED | Cary AArias | CARY PINEY PLAINS 230KV - SWIFT CREEK 24KV | 4/15/2019 05:55 | 4/15/2019 06:20 | 5034028-1 | OCB - ABC FID: T5111B23 | 01 Feeder Breaker/Recl in Substa | UG Distribution Line Underground | 20 Equipment failure | DC Insulation Failure | 56 Sectionalized/Restored Servic | U1 Cable, UG, Primary | UN Unknown Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,356 | 1457 | 25 | Line~13XG94_CAX48_2787417 | Undergrnd Fac Underground Primary Failure Cable Failed BAD UG 750 between H424K AND CAX48 | aarias// storm in area. 750 UG primary failed. Normal feed comes out of Roylene 23KV, was backfed from Swift Creek to isolate outage at Roylene (see tkt 5033619). No pictures 5034028-1 feeder outage 5034028-2 opened feeder tie switch at H392K 5034028-3 opened recloser at 1CEQ10 ~~~ 4/17/2019 ¦ AArias ¦ Investigative Action
Dist - MED | Cary omshistproc | RALEIGH OAKDALE 230KV - PLAZA WEST 23KV | 4/15/2019 06:15 | 4/15/2019 06:23 | 5034050 | RECLOSER - ABC FID: 1CEK29_113479046 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 524 | 3276 | 8 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
Dist - MED | Cary C80721 | CARY 230KV - WEST CHATHAM STREET 23KV | 4/15/2019 14:48 | 4/15/2019 16:26 | 5034561-1 | SWITCH - ABC FID: E452K_2660361 | 08 Disconnect | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 47 Replaced Pole | P1 Pole, Creosote | UU Unknown Manufacturer |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 3,163 | 3395 | 98 | Line~RA713_RA714_2641277 | Overhead Fac Pole Failure Burned pole ra713 burned down | aarias// storm in area. Crossarm bracket failed on double pole line and caused pole top to catch on fire. Pole replaced. Cary feeder outage ticket 5034600-2 Cust Counts reviewed for accuracy in Cyme with BL 5034561-1: backfed from the Triangle Forest feeder 5034561-2: sectionalized damage 5034561-3: W Chatham St 23KV feeder outage 5034600-2: Cary 23KV feeder outage ~~~ 4/15/2019 ¦ C80721 ¦ Investigative Action
Dist - MED | Cary omshistproc | CARY 230KV - WEST CHATHAM STREET 23KV | 4/15/2019 14:49 | 4/15/2019 15:24 | 5034535 | SWITCH - A FID: 8910K_2702408 | 08 Disconnect |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 2,096 | 3395 | 35 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
Dist - MED | Cary AArias | CARY 230KV - CARY 23KV | 4/15/2019 15:32 | 4/15/2019 16:23 | 5034600-1 | RECLOSER - ABC FID: 9479K_107922848 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | D4 Burned/Exploded | 47 Replaced Pole | P1 Pole, Creosote | UU Unknown Manufacturer |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,374 | 1574 | 51 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None pole burned | aarias// storm in area. Crossarm bracket failed (non-veg related) on double pole line and caused pole top to catch on fire. Pole replaced. Outage ticket 5034561-1: backfed W Chatham St 23KV from the Triangle Forest 23KV feeder 5034561-2: sectionalized damage on W Chatham St 23KV 5034561-3: W Chatham St 23KV feeder outage 5034600-1: backfed Cary 23KV from the Walnut Hills 23KV feeder 5034600-2: Cary 23KV feeder outage 5034600-3: sectionalized damage on Cary 23KV 5034600-4: sectionalized damage on Cary 23KV ~~~ 4/15/2019 ¦ AArias ¦ Investigative Action
Dist | Garner c72037 | CARALEIGH 230KV - CAROLINA PINES 24KV | 4/16/2019 11:16 | 4/16/2019 12:21 | 5034838-2 | SWITCH - ABC FID: 13DN06_2894274 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA | NA R |  | F2 Forced Outage | 00 Calm | 603 | 3254 | 65 | HN21BJ | Human Interf OH - Vehicle None CAR HIT POLE @ HN21BJ | MHS- A tractor trailer went off the edge of the road loosing control and hitting our pole, breaking it at ground level. Crew did switching and got all but 127 customers back on. Crew then replaced the pole ~~~ 4/24/2019 ¦ c72037 ¦ Investigative Action
Dist | Cary c72037 | NEW HILL 230KV - NEW HILL 23KV | 4/18/2019 15:32 | 4/18/2019 16:32 | 5035499-2 | SWITCH - ABC FID: CAD92_103607422 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair | P1 Pole, Creosote | NA R |  | F2 Forced Outage | 00 Calm | 801 | 1223 | 60 | 8086K | Human Interf OH - Vehicle None Truck hit pole #8086K breaking pole top. | MHS- truck hit pole, breaking top of pole. Crew cut top of pole out and installed cross arm and bringing pole up to spec. ~~~ 4/23/2019 ¦ c72037 ¦ Investigative Action
Dist - MED | Durham dlm4375 | POPE ROAD - 14082403 | 4/19/2019 11:01 | 4/19/2019 13:38 | 111802881 | S-RCL - ABC Size: 800 VPST FID: 38998783 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 08 Error, Duke | DR Roots rotten/defective | FS FLISR System | OA Oak | 60 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,345 | 3227 | 157 | behind 23-29 Stoneridge Circle | CMPL 2019-04-19 13:41:00 by LWG9380 RMK: RECL OUTAGE...3 80 t took reclosure out it appears | dlm4375.med day.storm in area.self healing circuit..crew refused 80T's see 11180638 due to defective oak tree 60'rotten/defective at root level on one side, that fell from private property bhnd 23-29 Stoneridge Circle taking down multiple spans of pri back property.Rec outage tickets see 111802881,111802882, 11183685, 11183675, 11183569, 11181900, 11181587, 11181336, 11180286, ..Self healing didn't operate correct sent email to DPAC to have coordination study (see email in outage pictures) done for self healing Team 74 Pope Rd 2403/Pope Rd 2410. Pope 2403 is disabled now after this outage also we have rec facid 38998783 bypassed.. Not sure if customer counts is even correct on outage tickets. did check times in roads... Investigation still underway***UPDATE AS OF 4/26/2019 from.. DPAC:ONE PROBLEM FOUND SO FAR:that none of these devices are modeled within DMS.NEED UPDATED CYME MODEL,NEED IP ADDRESSES FOR EACH DEVICES 13 OF THEM TO RETRIEVE SETTINGS..ENTIRE TEAM TO BE EVALUATED...still under investigation ~~~ 4/23/2019 ¦ dlm4375 ¦ Investigative Action
Dist - MED | Cary c72037 | RALEIGH SOUTH 115KV - LAKE DAM 23KV | 4/19/2019 11:41 | 4/19/2019 15:51 | 5035853-3 | RECLOSER - BC FID: 1C7H73_112359762 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA | NA R |  | F2 Forced Outage | 03 Wind | 1,660 | 2974 | 250 | Recloser~1C7H73 | Overhead Fac Undetermined Recloser Lockout nothing found. recloser in and holding. | MHS- Crew rode out line and could find nothing. they had DCC put the recloser on a one shot and give it a try. the recloser closed in and held. ~~~ 4/24/2019 ¦ c72037 ¦ Investigative Action
Dist - MED | Garner c72037 | CARALEIGH 230KV - SOUTH SAUNDERS 24KV | 4/19/2019 11:45 | 4/19/2019 14:21 | 5035864 | OCB - ABC FID: T4595B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA | NA R |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,067 | 1072 | 156 |  | Overhead Fac Undetermined Feeder Circuit Breaker Lockout | MHS- Crew rode out line and found nothing, they had DCC put it on a one shot and DCC give it a try. the FCB closed back in and held all 3 phases ~~~ 4/24/2019 ¦ c72037 ¦ Investigative Action
Dist - MED | Durham dlm4375 | POPE ROAD - 14082403 | 4/19/2019 22:56 | 4/20/2019 02:24 | 11183685 | S-RCL - ABC Size: 800 VPTT FID: 410935830 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | 08 Error, Duke | DR Roots rotten/defective | FS FLISR System | OA Oak | 60 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,503 | 3227 | 208 | behind 23-29 Stoneridge Circle | Outage from recloser at Randolph and Erwin not working. TL 516 VB | dlm4375.med day.storm in area.self healing circuit..crew refused 80T's see 11180638 due to defective oak tree 60'rotten/defective at root level on one side, that fell from private property bhnd 23-29 Stoneridge Circle taking down multiple spans of pri back property.Rec outage tickets see 111802881,111802882, 11183685, 11183675, 11183569, 11181900, 11181587, 11181336, 11180286, ..Self healing didn't operate correct sent email to DPAC to have coordination study (see email in outage pictures) done for self healing Team 74 Pope Rd 2403/Pope Rd 2410. Pope 2403 is disabled now after this outage also we have rec facid 38998783 bypassed.. Not sure if customer counts is even correct on outage tickets. did check times in roads... Investigation still underway***UPDATE AS OF 4/26/2019 from.. DPAC:ONE PROBLEM FOUND SO FAR:that none of these devices are modeled within DMS.NEED UPDATED CYME MODEL,NEED IP ADDRESSES FOR EACH DEVICES 13 OF THEM TO RETRIEVE SETTINGS..ENTIRE TEAM TO BE EVALUATED...still under investigation ~~~ 4/23/2019 ¦ dlm4375 ¦ Investigative Action
Dist | Chapel Hill rlw2159 | EASTGATE RET - 19021206 | 4/22/2019 15:23 | 4/22/2019 22:28 | 11185712 | SOH - ABC Size: 600 Line Disconnect FID: 84420415 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P1 Pole, Creosote |  |  | F2 Forced Outage | 00 Calm | 730 | 1096 | 425 | 500 WEAVER DAIRY RD | CMPL 2019-04-22 23:00:00 by CRBARWI RMK: OPENED SOLIDS 84420415 TO ENERGIZE CIRCUIT AND ISOLATE POLE AT PL: 363384412 - FAULTED RIGHT BEFORE LINE RECLOSER 39005400 | rlw2159-car broke pole, solid blades opened at FID# 84420415 to get circuit back on. ASSOCIATED tickets 11185597(blink), 11185600(circuit) and 11186136(open ckt to close solid blades ~~~ 4/24/2019 ¦ rlw2159 ¦ Investigative Action
Dist | Garner c72037 | WAKE TECH 230KV - TWIN CREEKS 24KV | 4/25/2019 01:19 | 4/25/2019 04:08 | 5039651-2 | SWITCH - ABC FID: 18RC00_110413460 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA | NA R |  | F2 Forced Outage | 00 Calm | 940 | 2433 | 169 | C289BH | Human Interf OH - Vehicle None broke in line feeder pole dis#C289BH | MHS-A car left the road striking and breaking pole # C289BH about 2 feet above ground level. crew did switching to get as many customers back on than changed out pole. ~~~ 5/2/2019 ¦ c72037 ¦ Investigative Action
Dist | Cary c72037 | RALEIGH SOUTH 115KV - LAKE DAM 23KV | 4/26/2019 14:20 | 4/26/2019 15:30 | 5040110-1 | RECLOSER - AC FID: 1C7H73_112359762 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA | NA R |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 904 | 2974 | 70 | Recloser~1C7H73_112359762 | Overhead Fac Undetermined Recloser Lockout DID NOT FIND ANYTHING | MHS- tech rode line out twice and found nothing on line. Had DCC put line under hot line tag and give it a one shot. Re-closer closed back in and held. ~~~ 8/1/2019 (97 days) ¦ c72037 ¦ Investigative Action
Dist | Asheboro i25781 | ASHEBORO EAST 115KV - ASHEBORO EAST HIGHWAY 64 23KV | 4/27/2019 12:11 | 4/27/2019 12:47 | 5041431 | RECLOSER - ABC FID: 1F1D21_115163773 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 43 Replaced Cutout and Fuse | 10 Sectionalizer | W2 Westinghouse |  | P4 Crew Initiated Outage | 03 Wind | 530 | 1751 | 36 | Line~L554AD_L589AD_2278942 | Overhead Fac Cutout/Fuse Link Failure Cutout Burned Up cutout burned up @ L589AD | JWW// When service tech arrived a cutout with solid blade disconnect was on fire so the service tech had DCC drop G&W at 12:11pm causing 530 customers to loose power. Service tech then replaced cutout and had DCC energize the G&W at 12:47pm restoring power to all customers. Pictures available. ~~~ 5/2/2019 ¦ i25781 ¦ Investigative Action
Dist | Asheboro i25781 | ASHEBORO SOUTH 115KV - ASHEBORO SOUTH 23KV | 4/30/2019 08:15 | 4/30/2019 10:11 | 5042044-1 | RECLOSER - ABC FID: 5092AD_114685448 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 1,367 | 1839 | 116 | Switch~P119AD_2305726 | Human Interf OH - Vehicle None Car hit pole broke pole in half at DIS 1119AD Car hit pole broke pole in half at DIS 1119AD | JWW// On 4/30/19 at 08:15am a car hit a 3 phase pole at P119AD and broke it locking out G&W at 5092AD causing 1367 people to loose power. Crew replaced pole and had DCC energized G&W at 10:11 restoring power to all 1367 people. ~~~ 5/7/2019 ¦ i25781 ¦ Investigative Action
Dist | Asheboro i25781 | ASHEBORO SOUTH 115KV - DIXIE DRIVE 23KV | 5/4/2019 17:38 | 5/4/2019 18:22 | 5043374-1 | OCB - ABC FID: T0950B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 39 Repaired Overhead Conductor | AS Sleeve, compression splice | UU Unknown Manufacturer |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,707 | 1760 | 44 | M507AD | Overhead Fac Overhead Primary Failure (No Tree Involved) Splice Failed Unsure of what happened. Wire was down at splice but end looked melted. Unsure of what happened. Wire was down at splice but end looked melted. | JWW// On 5/4/19 at 17:38 the road side phase of 2/0 copper pulled out of sleeve resulting in the Dixie Drive FDR locking out causing 1763 people to lose power. When the service tech arrived he opened up 3 solid blade disconnects at M509AD then had DCC energize FDR at 18:22 restoring power to 1707 customers. Crew made repairs and then energized the remaining 56 customers at 19:11. Pictures of splice available. ~~~ 5/7/2019 ¦ i25781 ¦ Investigative Action
Dist | Durham dlm4375 | ELLIS RD RET - 14192413 | 5/5/2019 16:29 | 5/5/2019 17:06 | 11206243 | SOH - ABC Size: 600 Line Disconnect FID: 356526526 | 08 Disconnect | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | MP Porcelain | 36 Cutout, fused |  |  | P4 Crew Initiated Outage | 02 Rain | 763 | 774 | 37 | W Cornwallis Rd UG Dip for Tri Center South | SOLIDS OPENED TO OPEN JUMPERS FOR ISOLATION EVNT 11206153 ...TL628 LATTA | dlm4375...reported by 911...circuit blink see 11206162..had a 65E facid 38794436 (feeds UG dip) SMU 27KV switch/cutout break down and a 40/3 double dead end pole catch pole on fire. Crew opened inlines see 11206243 with load break tool and cut Jumpers in see 11206277 (AT 65E) to isolate dip pole. Crew made safe, turned in follow up see WO#32541029. crew then dropped circuit see 11206274 to close inlines back. ~~~ 5/6/2019 ¦ dlm4375 ¦ Investigative Action
Dist | Garner e68825 | MILBURNIE 230KV - BELTLINE 23KV | 5/8/2019 16:56 | 5/8/2019 17:47 | 5045043 | OCB - ABC FID: T5000B44 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | 25 Improper Installation | 39 Repaired Overhead Conductor | HC Clamp, hot line | UU Unknown Manufacturer | 0 | F2 Forced Outage | 00 Calm | 1,098 | 1097 | 51 | B319BK | Overhead Fac Overhead Primary Failure (No Tree Involved) Conductor Broke/Burned Down LINE DOWN | Fontana 5/9/19 (Updated 5/10/19 Peel)- The aluminum hot line clamp directly connected on the middle phase (B-phase) connecting the SD CU riser to the #2 ACSR line conductor at UG riser pole B321BK, loosened over time and started arcing, destroying the HLC and burned the wire in two, allowing the energized phase conductor to drop onto and entangled into the span neutral conductor, creating a B-phase to ground fault at pole B319BK. Since this tap was not fused at the feeder pole, the fault locked out the FCB. C&M repaired the phase conductor at the break, reconnected the SD CU riser with a new HLC, then had DCC close the FCB to restore service to the feeder. A work order is being generated to rebuild the feeder pole B319BK to add fused cutouts for the OH tapline to prevent recurrence. ~~~ 5/9/2019 ¦ e68825 ¦ Investigative Action
Dist | Cary c72037 | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 5/15/2019 09:27 | 5/15/2019 10:19 | 5047033 | RECLOSER - ABC FID: A194_104369660 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA | NA R |  | F2 Forced Outage | 00 Calm | 1,897 | 2927 | 52 | Recloser~A194_104369660 | Missing Missing Missing | MHS- crew rode out line and could not find nothing, they had DCC try the recloser and it held. rode the line out and found 13 spots where trees were burning in the primary. Did a W/O 32701128 to trim trees ~~~ 5/20/2019 ¦ c72037 ¦ Work Order(s) Generated
Dist | Garner c72037 | ANGIER 230KV - PEARIDGE 23KV | 5/19/2019 16:22 | 5/19/2019 18:02 | 5048056-1 | SOURCE - ABC FID: G672_2777110 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 52 Restored From Alternate Sourc | S9 Breaker | NA R |  | F2 Forced Outage | 00 Calm | 942 | 2415 | 100 | Switch~T5427B04 | Transmission Substation Equipment Outage Feeder Circuit Breaker breaker will not close back in rode and found nothing so far | MHS- Substation Equipment, Feeder breaker had the trip coil fail and burn up. the crew off loaded the Pearidge feeder onto the Kennebec feeder. do not have a date at this time when it will be repaired. ~~~ 5/21/2019 ¦ c72037 ¦ Investigative Action
Dist | Garner c72037 | ANGIER 230KV - PEARIDGE 23KV | 5/19/2019 16:22 | 5/19/2019 18:07 | 5048056-2 | SOURCE - ABC FID: P762BH_104370309 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 52 Restored From Alternate Sourc | S9 Breaker | NA R |  | F2 Forced Outage | 00 Calm | 1,471 | 2415 | 105 | Switch~T5427B04 | Transmission Substation Equipment Outage Feeder Circuit Breaker breaker will not close back in rode and found nothing so far | MHS- Substation Equipment, Feeder breaker had the trip coil fail and burn up. the crew off loaded the Pearidge feeder onto the Kennebec feeder. do not have a date at this time when it will be repaired. ~~~ 5/21/2019 ¦ c72037 ¦ Investigative Action
Dist | Cary DFontan | CARY EVANS ROAD 230KV - NORTH HARRISON 24KV | 5/20/2019 11:36 | 5/20/2019 12:29 | 5048249-1 | OCB - ABC FID: T4602B03 | 01 Feeder Breaker/Recl in Substa | UG Distribution Line Underground | 09 Public Accident/Damage | HD Accident, public dig-in | 56 Sectionalized/Restored Servic | UR Cable, UG, 25KV 750 MCM |  |  | F2 Forced Outage | 00 Calm | 1,394 | 1856 | 53 | 1CAL73_C246K | Human Interf Dig-Ins Primary Cable | Fontana 6/27/19 - Boring crew for cable company dug into A-phase of the UG 750 cable on Weston Parkway between 1CAL73 and C246K. Unable to get any photos since boring work has since been completed. Crew switched out the damaged section, closed back in the breaker and tied the remained of the feeder to the Silverton circuit by closing compartment 1 in PMH E435K. ~~~ 6/27/2019 (38 days) ¦ DFontan ¦ Investigative Action
Dist | Cary DFontan | CARY EVANS ROAD 230KV - NORTH HARRISON 24KV | 5/20/2019 11:36 | 5/20/2019 12:52 | 5048249-2 | SWITCH - ABC FID: E435K_2650592 | 08 Disconnect | UG Distribution Line Underground | 09 Public Accident/Damage | HD Accident, public dig-in | 56 Sectionalized/Restored Servic | UR Cable, UG, 25KV 750 MCM |  |  | F2 Forced Outage | 00 Calm | 606 | 1856 | 76 | Line~1CAL73_C246K_112854148 | Human Interf Dig-Ins Primary Cable | Fontana 6/27/19 - Boring crew for cable company dug into A-phase of the UG 750 cable on Weston Parkway between 1CAL73 and C246K. Unable to get any photos since boring work has since been completed. Crew switched out the damaged section, closed back in the breaker and tied the remained of the feeder to the Silverton circuit by closing compartment 1 in PMH E435K. ~~~ 6/27/2019 (38 days) ¦ DFontan ¦ Investigative Action
Dist | Cary DFontan | AMBERLY 230KV - YATES STORE 24KV | 5/21/2019 12:47 | 5/21/2019 13:45 | 5048626 | RECLOSER - BC FID: 13K853_104269112 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 28 Patrolled & No Problem Found | NA |  |  | F2 Forced Outage | 00 Calm | 895 | 1895 | 58 |  | Overhead Fac Undetermined Recloser Lockout Nothing was found while riding out the feeder. | Fontana 6/26/19 - C&M responder was unable to find anything during his patrol and ultimately had DCC close the recloser back in. An FMS/Cyme analysis was performed which identified a B-C phase fault between 1690K and 1687K. After a thorough patrol there was no definitive cause for the fault that could be found. Between poles 1689K and B057K, however, there were numerous trees burning in the line. It is possible this could have lead to the lockout. ~~~ 6/26/2019 (36 days) ¦ DFontan ¦ Investigative Action
Dist | Cary DFontan | APEX 230KV - APEX HIGHWAY 55 23KV | 5/24/2019 12:33 | 5/24/2019 13:32 | 5049580-1 | RECLOSER - ABC FID: 9RK98_104607789 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 00 Calm | 1,923 | 2093 | 59 | Recloser~9RK98_104607789 | Overhead Fac Undetermined Recloser Lockout Under Hot Line Tag (Comments) NO CREW INVOLVEMENT ON LOCKOUT. DEP CREWS PATROLLING. | Fontana 6/26/19 - Recloser was under hot line tag but according to C&M no crew was actually working on the line when the lockout occurred. FMS/Cyme analysis proved to be inconclusive as the fault magnitude was too low to provide a fault location Cyme. Cyme indicated a low magnitude C-phase to GND fault which likely was from the wind briefly blowing a tree into the primary. Official cause is unknown. Since crew wasn't working on line during trip, C&M assumed there was a permanent fault and began switching. They closed in N.O recloser 113A60 to tie the feeder in with the Wimberly Road Circuit ~~~ 6/26/2019 (33 days) ¦ DFontan ¦ Investigative Action
Dist | Cary DFontan | APEX 230KV - APEX HIGHWAY 55 23KV | 5/24/2019 12:33 | 5/24/2019 13:36 | 5049580-2 | RECLOSER - ABC FID: 113A60_104576764 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 00 Calm | 1,473 | 2093 | 63 | Recloser~9RK98_104607789 | Overhead Fac Undetermined Recloser Lockout Under Hot Line Tag (Comments) NO CREW INVOLVEMENT ON LOCKOUT. DEP CREWS PATROLLING. | Fontana 6/26/19 - Recloser was under hot line tag but according to C&M no crew was actually working on the line when the lockout occurred. FMS/Cyme analysis proved to be inconclusive as the fault magnitude was too low to provide a fault location Cyme. Cyme indicated a low magnitude C-phase to GND fault which likely was from the wind briefly blowing a tree into the primary. Official cause is unknown. Since crew wasn't working on line during trip, C&M assumed there was a permanent fault and began switching. They closed in N.O recloser 113A60 to tie the feeder in with the Wimberly Road Circuit ~~~ 6/26/2019 (33 days) ¦ DFontan ¦ Investigative Action
Dist | Garner c72037 | RALEIGH WORTHDALE 230KV - PLAZA EAST 23KV | 5/28/2019 09:15 | 5/28/2019 09:51 | 5050538 | SWITCH - ABC FID: 2W494_1227381 | 08 Disconnect | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 56 Sectionalized/Restored Servic | AB Air Break | NA R |  | F2 Forced Outage | 00 Calm | 1,080 | 1794 | 36 | Switch~2W494 | Overhead Fac Overhead Switch / Recloser Failure Air Break Switch Failed | MHS-Service tech found Air break switch and pole on fire, he had DCC open up the FCB so he could open up the air break switch. he than had DCC close back in the FCB and restored remaining customers from back feed ~~~ 6/5/2019 ¦ c72037 ¦ Work Order(s) Generated
Dist | Garner c72037 | GARNER 115KV - CRESCENT 24KV | 5/29/2019 15:31 | 5/29/2019 17:57 | 5051185 | RECLOSER - A FID: 12PJ03_103837646 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA | NA R |  | F2 Forced Outage | 00 Calm | 1,001 | 2727 | 146 | N/A | Overhead Fac Undetermined Recloser Lockout switching to move load | MHS- crew had A phase of recloser 12PJ03 lock out while switching load crew road out line and could not find anything. crew had DCC put line under hot line tag and give it a one shot. recloser closed back in and held. ~~~ 6/5/2019 ¦ c72037 ¦ Investigative Action
Dist | Garner c72037 | DUNCAN 230KV - WILBON 24KV | 6/5/2019 16:10 | 6/5/2019 16:52 | 5055013 | RECLOSER - AB FID: 1DGJ03_115163579 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA | NA R |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,565 | 3456 | 42 |  | Missing Missing Missing | MHS- service tech road line out twice and could not find anything that could have locked out the recloser, so he had DCC put the recloser on a one shot and try it. the recloser held. there was lighting in the area at the time ~~~ 6/12/2019 ¦ c72037 ¦ Investigative Action
Dist | Durham rlw2159 | FAIRNTOSH - 14142410 | 6/6/2019 20:22 | 6/7/2019 03:36 | 11238190 | S-CKT - ABC Size: Class 2 FID: 38356473 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | 19 Lightning strike | 27 Other/See Notes | C1 Crossarm, Creosote |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 3,566 | 3589 | 434 | Old Oxford rd | CMPL 2019-06-07 04:16:00 by VDB7113 RMK: CIRCUIT LOCKOUT -..Techs riding out feeder, Fault llocations have been provided. No cause has been identified as of 20:30 06/06/19..Duty Supervisor aware | rlw2159-(storm in area)crews rode and inspected each pole several times and also tried the Station breaker 5 times trying to locate the fault. The crew eventually found a long 1 & 1/2 inch wide piece of cross arm from circuit 2405 that lighting had caused to fall across all 3 phases. This was difficult to locate due to rainy conditions and the positioning of the piece of arm. Blink ticket #s 11238190, 11238315, 11238308, 11238301, 11238274, 11238251 & 11238187 were all associated with outage ID# 11238364. ~~~ 6/10/2019 ¦ rlw2159 ¦ Investigative Action
Dist | Durham rlw2159 | FAIRNTOSH - 14142410 | 6/7/2019 03:56 | 6/7/2019 04:11 | 11238353 | S-CKT - ABC Size: Class 2 FID: 38356473 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 07 Proactive Work | 37 Removed Limb or Tree From Lin |  |  |  | P5 No Customer Notification | 04 Wind, Rain and Lightning | 3,565 | 3589 | 15 | BETWEEN 1915 OLD OXFORD AND STANLEY RD | EMERGENCY DROP / TREE BURNING IN LINES AFTER ENERGIZING CIRCUITS BACK UP | rlw2159-I REQUESTED 2405 AND 2410 OUT OF FAIRNTOSH BE DROPPED AFTER OUTAGE ID# 11238190 WAS RESTORED DUE TO A TREE FROM OUT OF THE ROW HAVING LEANED OVER INTO CIRCUIT 2405 AND BURNING. THIS DECISION WAS MADE DUE TO THIS TREE WOULD HAVE TAKEN THESE CIRCUITS OUT IN ONE OF THE NEXT HEAVY RAINS WE HAD. ~~~ 6/10/2019 ¦ rlw2159 ¦ Investigative Action
Dist | Garner c72037 | GARNER I-40 230KV - NEW HOPE 24KV | 6/8/2019 03:10 | 6/8/2019 07:47 | 5056297 | RECLOSER - ABC FID: 143508_105710363 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | DE Prior damage | M2 ACSR | 29 Conductor, bare | NA R |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,079 | 2776 | 277 | Line~HY08BJ_HY11BJ_1167889 | Overhead Fac Overhead Primary Failure (No Tree Involved) Conductor Broke/Burned Down wire off insulator at hy08bj wire off insulator | MHS- crew found wire had come off of insulator at DIS# HY08BJ and burnt down locking out recloser 143508. crews did repairs then had DCC re-energize the recloser. there was an outage 5050458 on 5/28/2019 one pole down were pole and wire was down on the ground. ~~~ 6/12/2019 ¦ c72037 ¦ Investigative Action
Dist | Chapel Hill rlw2159 | JAMES ST - 19031207 | 6/13/2019 12:40 | 6/13/2019 18:12 | 11249610 | S-RCL - ABC Size: 560 WVE FID: 39008813 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | DC Insulation Failure | 16 Closed Recl or Sectionalizer | UG Cable, UG, 25KV 1/0 |  |  | F2 Forced Outage | 00 Calm | 633 | 2058 | 332 |  | CIRCUIT LOCKOUT TARGETS B-G FMAG 2217 ..TARGETS RESET ..FAULT HALOS W. POPLAR AVE BETWEEN BLACKWOOD AND LILAC....FAULT HALOS HILLSBOROUGH RD NEAR GREENSBORO RD... FAULT HALOS N. GREENSBORO RD NEAR OAK ST. | rlw2159--ckt outage 11249149 is related. Crew opened recloser to get circuit back on. re-energized once circuit was re-energized. Outage ticket 11249657 was the reason the blocked circuit went out. ~~~ 6/13/2019 ¦ rlw2159 ¦ Investigative Action
Dist | Chapel Hill rlw2159 | JAMES ST - 19031207 | 6/13/2019 12:40 | 6/13/2019 18:10 | 11249609 | RCL - ABC Size: 200 L FID: 39008809 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | DC Insulation Failure | 16 Closed Recl or Sectionalizer | UG Cable, UG, 25KV 1/0 |  |  | F2 Forced Outage | 00 Calm | 728 | 2058 | 330 |  | CIRCUIT LOCKOUT TARGETS B-G FMAG 2217 ..TARGETS RESET ..FAULT HALOS W. POPLAR AVE BETWEEN BLACKWOOD AND LILAC....FAULT HALOS HILLSBOROUGH RD NEAR GREENSBORO RD... FAULT HALOS N. GREENSBORO RD NEAR OAK ST. | rlw2159--ckt outage 11249149 is related. Crew opened recloser to get circuit back on. re-energized once circuit was re-energized. The 100k fuse blew on Outage ticket 11249657 when this recloser was energized. This recloser was opened to get the circuit back on ticket# 11249149. ~~~ 6/18/2019 ¦ rlw2159 ¦ Investigative Action
Dist | Chapel Hill rlw2159 | JAMES ST - 19031207 | 6/13/2019 12:40 | 6/13/2019 18:21 | 11249608 | RCL - ABC Size: 200 V4L FID: 39005368 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | DC Insulation Failure | 16 Closed Recl or Sectionalizer | UG Cable, UG, 25KV 1/0 |  |  | F2 Forced Outage | 00 Calm | 512 | 2058 | 341 |  | CIRCUIT LOCKOUT TARGETS B-G FMAG 2217 ..TARGETS RESET ..FAULT HALOS W. POPLAR AVE BETWEEN BLACKWOOD AND LILAC....FAULT HALOS HILLSBOROUGH RD NEAR GREENSBORO RD... FAULT HALOS N. GREENSBORO RD NEAR OAK ST. | rlw2159--ckt outage 11249149 is related. Crew opened recloser to get circuit back on. re-energized once circuit was re-energized. Outage ticket 11249657 was the reason the blocked circuit went out. ~~~ 6/13/2019 ¦ rlw2159 ¦ Investigative Action
Dist | Garner c72037 | GARNER I-40 230KV - NEW HOPE 24KV | 6/13/2019 23:15 | 6/14/2019 03:29 | 5059001-4 | RECLOSER - ABC FID: 143508_105710363 | 08 Disconnect | UG Distribution Line Underground | 20 Equipment failure | DC Insulation Failure | 40 Repaired Underground Service | UA Cable, UG, 15KV 750 MCM | NA R |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 503 | 2776 | 254 | Recloser~10WF93 | Undergrnd Fac Underground Primary Failure Cable Failed | MHS- crew rode the line out and found nothing, they had DCC open the A & C phase and test recloser at 10WF93 and when B phase locked out again they started looking at the 750 underground. they found a bad span of 750 from did# 57D35 to HU46BJ.crew did some switching to get all customers back on. U/G crew did repair, then we did w/o 33051854 to replace. 1989 cable ~~~ 6/20/2019 ¦ c72037 ¦ Work Order(s) Generated
Dist | Garner c72037 | GARNER I-40 230KV - NEW HOPE 24KV | 6/14/2019 02:34 | 6/14/2019 03:28 | 5059068-2 | SWITCH - ABC FID: HT11BJ_1227142 | 08 Disconnect | UG Distribution Line Underground | 11 Unknown Cause | DC Insulation Failure | 40 Repaired Underground Service | UA Cable, UG, 15KV 750 MCM | NA R |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 576 | 2776 | 54 | Line~HU46BJ_57D35 | Missing Missing Missing | MHS- crew rode the line out and found nothing, they had DCC open the A & C phase and test recloser at 10WF93 and when B phase locked out again they started looking at the 750 underground. they found a bad span of 750 from did# 57D35 to HU46BJ.crew did some switching to get all customers back on. U/G crew did repair, then we did w/o 33051854 to replace. 1989 cable ~~~ 6/20/2019 ¦ c72037 ¦ Work Order(s) Generated
Dist | Durham rlw2159 | FAIRNTOSH - 14142410 | 6/22/2019 03:14 | 6/22/2019 04:00 | 11260882 | S-CKT - ABC Size: Class 2 FID: 38356473 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | ED Erosion/Washout | 37 Removed Limb or Tree From Lin |  | OA Oak | 30 | P2 Scheduled Outage | 02 Rain | 3,563 | 3589 | 46 | P3OH: 34256232 | DCC OPENED BREAKER SO CREWS COULD REMOVE TREE FROM LINE THAT WAS BURNING - FAULT LOCATION P3OH: 34256232 | rlw2159-oak tree from out of ROW fell over onto double circuit primary(could not determine exactly how far away as I couldn't get through the thicket-DCC OPENED BREAKER SO CREWS COULD REMOVE TREE FROM LINE THAT WAS BURNING - FAULT LOCATION P3OH: 34256232 ~~~ 7/2/2019 ¦ rlw2159 ¦ Investigative Action
Dist | Garner c72037 | GARNER 115KV - VANDORA SPRINGS 24KV | 6/24/2019 08:20 | 6/24/2019 10:12 | 5065540-2 | RECLOSER - ABC FID: 146W86_113087425 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 17 Tree error, public | DN No apparent defect | C1 Crossarm, Creosote | PT PINE | 18 | F2 Forced Outage | 00 Calm | 1,484 | 2307 | 112 | Line~DE27BJ_140C98_2894076 | Human Interf Tree Cut on Line (By Logger or Customer) None back on | MHS- Tree Cut on Line (By Logger or Customer) taking down all phases of primary and breaking cross arm. crew did switching to restore all but 153 customers till repairs were done ~~~ 6/27/2019 ¦ c72037 ¦ Investigative Action
Dist | Garner c72037 | GARNER 115KV - VANDORA SPRINGS 24KV | 6/24/2019 08:20 | 6/24/2019 09:11 | 5065540-1 | OCB - ABC FID: T4720B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 17 Tree error, public | DN No apparent defect | C1 Crossarm, Creosote | PT PINE | 18 | F2 Forced Outage | 00 Calm | 557 | 2307 | 51 | Line~DE27BJ_140C98_2894076 | Human Interf Tree Cut on Line (By Logger or Customer) None back on | MHS- Tree Cut on Line (By Logger or Customer) taking down all phases of primary and breaking cross arm. crew did switching to restore all but 153 customers till repairs were done ~~~ 6/27/2019 ¦ c72037 ¦ Investigative Action
Dist | Garner c72037 | GARNER 115KV - RANDS MILL 24KV | 6/24/2019 11:01 | 6/24/2019 11:13 | 5065632 | RECLOSER - ABC FID: 1CBW41_113087071 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 16 Closed Recl or Sectionalizer | 39 Disconnect | NA R |  | F2 Forced Outage | 00 Calm | 894 | 2586 | 12 | 17YD65 | Overhead Fac Overhead Switch / Recloser Failure In-Line Disconnect Failed | MHS- Service tech found disconnect at 17YD65 open and arching need to replace 600 amp disconnects. ~~~ 6/27/2019 ¦ c72037 ¦ Work Order(s) Generated
Dist | Cary DFontan | CARY TRIANGLE FOREST 230KV - PARKWAY 23KV | 6/24/2019 13:26 | 6/24/2019 14:39 | 5065710-1 | OCB - ABC FID: T4605B01 | 01 Feeder Breaker/Recl in Substa | UG Distribution Line Underground | 09 Public Accident/Damage | HD Accident, public dig-in | 61 Google Fiber Project | UR Cable, UG, 25KV 750 MCM | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 2,252 | 2334 | 73 | AAL63K | Human Interf Dig-Ins Primary Cable | Fontana 6/25/19 - Google fiber jackhammered into B-phase of the UG 750 primary at 106 Arlington Ridge near XFMR AAL63K. Serviceman isolated and tagged out the 750 by opening up at PMH 12184 COMP 1 and AAL67K COMP 1. The remainder of the circuit was switched over to Macarthur 23kV feeder. ~~~ 6/25/2019 ¦ DFontan ¦ Investigative Action
Dist | Cary DFontan | CARY 230KV - CHAPEL HILL ROAD 23KV | 6/27/2019 10:18 | 6/27/2019 11:11 | 5066841 | OCB - ABC FID: T4600B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | 30 Error, Duke Contractor | 37 Removed Limb or Tree From Lin | NA |  |  | F2 Forced Outage | 00 Calm | 3,357 | 3435 | 53 | R319K | Human Interf OH - PE Contract Crew (Comments) PE Tree Contractor Crew BURFORD TREE CREW DROPPED TREE LIMB ACROSS FEEDER LOCKING OUT FCB | Fontana 6/28/19 - Burford tree crew performing routine tree trimming on the Chapel Hill Road feeder dropped a limb across all three phases of the primary near pole R319K. ~~~ 6/28/2019 ¦ DFontan ¦ Investigative Action
Dist | Cary DFontan | CARY EVANS ROAD 230KV - SILVERTON 24KV | 6/29/2019 09:24 | 6/29/2019 13:02 | 5067325-3 | SWITCH - ABC FID: 105528_2662526 | 08 Disconnect | UG Distribution Line Underground | 20 Equipment failure | DC Insulation Failure | MA Aluminum | UA Cable, UG, 15KV 750 MCM |  | 1 | F2 Forced Outage | 00 Calm | 1,648 | 1586 | 218 | 109B38 | Undergrnd Fac Underground Primary Failure Cable Failed fault in manhole @ 109B38 | Fontana 7/1/19 - UG 750 primary failed in manhole 109B38 located directly in front of a PMH. C&M responder was unable to go into manhole since it was filled with water and a vault crew had to be sent to pump out the manhole. He switched the remainder of the feeder onto the Royal Oaks, Evans Road, and Weston Feeders. UG crew to repair to repair cable. ~~~ 7/2/2019 ¦ DFontan ¦ Investigative Action
|  | MED DATE | MED TYPE
|  | 2019-04-15 | MED
|  | 2019-04-19 | MED
|  | 2019-06-20 | MED