## OUTFUN500
# | Category | Op Center | Circuit | Time Off | Time On | Outage ID | Device & Ph | Clearing Device | Resp. System | Cause (IEEE) | Failure Mode | AT/D/M | Eq. Code | Manuf./ Species | Cnt | Planned Outages | WE | # Cust | Ckt Cust | Dur | Fault Location | Crew Remarks | Additional Remarks
1 | Sub/T | Greensboro cag4361 | DENNY ROAD - 09252409 | 4/12/2019 15:32 | 4/12/2019 16:45 | 11170563 | S-CKT - ABC Size: Class 3 FID: 38357373 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | DF Fail to Reclose | 29 Permanent Repair | 28 Other Equipment |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,500 | 2516 | 73 | INTERSECTION OF DENNY RD AND MIZELL RD | CMPL 2019-04-12 16:51:00 by WCHODGI RMK: TCC ENROUTE TO BREAKER FOR FAILURE TO CLOSE ALARM - BRIAN PIERCY TESTING RELAY // BC TARGETS 3102// POSS FAULT LOCATION MIZELL RD BETWEEN DENNY RD AND LEES CHAPEL RD / RELAY TESTED GOOD | cag4361 circuit locked on 1 trip BG target. Lightning strike at area at same time. 3 lightning arrester fuses blown. Denny Road 2411 also tripped 1 time but did not lock out. 2411 and 2409 ride the same pole line also tripped at same time. ~~~ 4/26/2019 ¦ cag4361 ¦ Investigative Action
2 | Sub/T - MED | RURAL HALL skh9815 | RURAL HALL - 03281204 | 4/19/2019 14:47 | 4/19/2019 18:59 | 11181001 | S-CKT - ABC Size: Class EX FID: 38349933 | 00 Substation device | 00 Substation | 20 Equipment failure | D1 Broken/Malfunctioning | 14 Closed Breaker | S9 Breaker |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,619 | 1616 | 252 | Rural Hall Substation, inside fence | TRANSMISSION OUTAGE - POSSIBLE HT BREAKER MATT TUTTLE 336 314 3682 FROM TRANSMISSION EN ROUTE AS OF 1512 / no backfeeding options / civil crew to c/o breaker | Breaker failed to open due to temporary fault on 1204, causing high tension breaker to open/tech found bad capacitor trip on breaker/had to wait until new part was replaced on breaker/transmission doing further investigation/breakers will be modified at Rural Hall substation per Sangbo/no fu reqr skh9815 RURAL HALL RET 1204 BREAKER NEEDED REPAIR INSIDE STATION - CREW ATTEMPTED TO CLOSE BUT DID NOT HOLD 1ST TIME - MISSED ETR ~~~ 4/22/2019 ¦ skh9815 ¦ Investigative Action
3 | Sub/T - MED | Chapel Hill rlw2159 | EFLAND - 19241202 | 4/19/2019 16:10 | 4/19/2019 18:14 | 11181871 | S-CKT - ABC Size: Class 3 FID: 38358957 | 01 Feeder Breaker/Recl in Substa | 00 Substation | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | PT PINE | 25 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,784 | 1784 | 124 |  | Limb across all three phases near intersection of Redman Rd. and US 70 | rlw2159-(MED DAY) CREW REMOVED PINE LIMB FROM 3 PHASE PRIMARY. PINE LIMB APRROXIMATELY 3" IN DIAMETER AND 25' FROM CENTER LINE. ~~~ 4/23/2019 ¦ rlw2159 ¦ Investigative Action
4 | Sub/T - MED | LEWISVILLE pmb4141 | TURNERSBURG RET - 03651202 | 4/26/2019 15:55 | 4/27/2019 04:32 | 11192273 | S-CKT - ABC Size: Class 1A FID: 38350989 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | DZ Broken below Power Zone | 47 Replaced Pole | PP Pole | MP Maple | 52 | F2 Forced Outage | 03 Wind | 1,067 | 1066 | 757 | Between structures 15 & 16 & 81 | TRANSMISSION OUTAGE - TRANSMISSION OUTAGE -Transmission Feeder line to Turnersburg and Hager Rd is down, Crews working to have restored 04/27 @ 0300 AM --- | Stony Point - Lookout Tie, pmb4141, (2 incidents) Structure 81 of the main line was found broken below the power zone. Pole was rotten, believed high winds broke it in half. A maple tree from outside the R/W, about 35 ft. was found holding the conductor on the ground between structures 15 and 16 of Turnersburg Tap line. Tree was removed and pole was replaced. A work order review was completed and thereÃÂ's a list of 19 work orders for rotten poles to be replaced on the Stony Point Lookout line. Work Order Email List attached in TOMS, STR-81 was in the list. additional info on TOMS, per/ T. Mosteller. Pics in folder. Additionally, Turnersburg 1202 was not reenergized until storm events on the distribution side were completed, per/ R. Snyder. ~~~ 4/29/2019 ¦ pmb4141 ¦ Investigative Action
5 | Sub/T - MED | LEWISVILLE pmb4141 | TURNERSBURG RET - 03651203 | 4/26/2019 15:55 | 4/27/2019 00:24 | 11192275 | S-CKT - ABC Size: Class 1 FID: 38351013 | 11 Transmission device | 11 Transmission | 03 Vegetation | DZ Broken below Power Zone | 47 Replaced Pole | PP Pole | MP Maple | 35 | F2 Forced Outage | 03 Wind | 757 | 755 | 509 | Between structures 15 & 16 & 81 | TRANSMISSION OUTAGE - -Transmission Feeder line to Turnersburg and Hager Rd is down, Crews working to have restored 04/27 @ 0300 AM | Stony Point - Lookout Tie, pmb4141, (2 incidents) Structure 81 of the main line was found broken below the power zone. Pole was rotten, believed high winds broke it in half. A maple tree from outside the R/W, about 35 ft. was found holding the conductor on the ground between structures 15 and 16 of Turnersburg Tap line. Tree was removed and pole was replaced. A work order review was completed and there's a list of 19 work orders for rotten poles to be replaced on the Stony Point Lookout line. Work Order Email List attached in TOMS, STR-81 was in the list. additional info on TOMS, per/ T. Mosteller. Pics in folder. Additionally, Turnersburg 1202 was not reenergized until storm events on the distribution side were completed, per/ R. Snyder. ~~~ 4/29/2019 ¦ pmb4141 ¦ Investigative Action
6 | Sub/T - MED | LEWISVILLE pmb4141 | HAGER RD RET - 03661202 | 4/26/2019 15:55 | 4/27/2019 00:15 | 11192287 | S-CKT - ABC Size: Class 3 FID: 38351037 | 11 Transmission device | 11 Transmission | 03 Vegetation | DZ Broken below Power Zone | 47 Replaced Pole | PP Pole | MP Maple | 35 | F2 Forced Outage | 03 Wind | 525 | 523 | 500 | Between structures 15 & 16 & 81 | TRANSMISSION OUTAGE -Transmission Feeder line to Turnersburg and Hager Rd is down, Crews working to have restored 04/27 @ 0300 AM | Stony Point - Lookout Tie, pmb4141, (2 incidents) Structure 81 of the main line was found broken below the power zone. Pole was rotten, believed high winds broke it in half. A maple tree from outside the R/W, about 35 ft. was found holding the conductor on the ground between structures 15 and 16 of Turnersburg Tap line. Tree was removed and pole was replaced. A work order review was completed and there'ÃÂÃÂÃÂÃÂÃÂÃÂÃÂÃÂs a list of 19 work orders for rotten poles to be replaced on the Stony Point Lookout line. Work Order Email List attached in TOMS, STR-81 was in the list. Additional info on TOMS, per/ T. Mosteller. Pics in folder. ~~~ 4/29/2019 ¦ pmb4141 ¦ Investigative Action
7 | Sub/T - MED | LEWISVILLE pmb4141 | HAGER RD RET - 03661203 | 4/26/2019 15:55 | 4/27/2019 00:13 | 11192270 | S-CKT - ABC Size: Class 3 FID: 38351049 | 11 Transmission device | 11 Transmission | 03 Vegetation | DZ Broken below Power Zone | 47 Replaced Pole | PP Pole | MP Maple | 35 | F2 Forced Outage | 03 Wind | 1,038 | 1036 | 498 | Between structures 15 & 16 & 81 | TRANSMISSION OUTAGE -TRANSMISSION OUTAGE -Transmission Feeder line to Turnersburg and Hager Rd is down, Crews working to have restored 04/27 @ 0300 AM | Stony Point - Lookout Tie, pmb4141, (2 incidents) Structure 81 of the main line was found broken below the power zone. Pole was rotten, believed high winds broke it in half. A maple tree from outside the R/W, about 35 ft. was found holding the conductor on the ground between structures 15 and 16 of Turnersburg Tap line. Tree was removed and pole was replaced. A work order review was completed and there's a list of 19 work orders for rotten poles to be replaced on the Stony Point Lookout line. Work Order Email List attached in TOMS, STR-81 was in the list. additional info on TOMS, per/ T. Mosteller. Pics in folder. ~~~ 4/29/2019 ¦ pmb4141 ¦ Investigative Action
8 | Sub/T - MED | MT AIRY sba8312 | LEVEL CROSS - 28041201 | 4/26/2019 16:43 | 4/26/2019 20:49 | 11193259 | S-CKT - ABC Size: Class 3 FID: 38351397 | 01 Feeder Breaker/Recl in Substa | 00 Substation | 11 Unknown Cause | DF Fail to Reclose | 14 Closed Breaker | S9 Breaker |  |  | F2 Forced Outage | 17 Wind and Rain | 964 | 961 | 246 | inside Substation | CMPL 2019-04-26 20:53:00 by BLSOUTH RMK: CIRCUIT LOCKOUT | Breaker failed to reclose, Station Operator performed the Relay Trip Path Testing without any issues and so the breaker was placed back in-service .... the charging motor (specifically Ã¢ÂÂ the actuating switch) on Circuit Breaker 1201 wouldnÃ¢ÂÂt consistently charge the breaker after consecutive multiple operations due to contamination. After thoroughly cleaning/lubricating the motor, they were able to perform multiple breaker operations without any issues. No Pics available ~~~ 5/7/2019 ¦ sba8312 ¦ Investigative Action
9 | Sub/T | Reidsville gla4211 | GATEWOOD - 17131203 | 5/8/2019 03:52 | 5/8/2019 05:17 | 11208416 | S-CKT - ABC Size: Class 3 FID: 38358633 | 11 Transmission device | 11 Transmission | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J8 Raccoon |  | F2 Forced Outage | 00 Calm | 1,337 | 1338 | 85 | Sadler Tie | ECC TECH BRIAN PIERCY 336-823-1454 RESPONDING - TRANSMISSION OUTAGE - MEADOW SUMMIT 1 & 2, RUFFIN AND VANGAURD 45KV LINES ARE OUT - ECC INVESTIGATING - RACCOON GOT ON 44KV BUS INSIDE SWITCHING STATION CAUSING ALL FOUR TRANSMISSION LINES TO LOCKOUT | G Akers .. Comments from Joe Lambeth. ÂThe Sadler Tie 44KV Yellow Bus experienced an interruption this morning at 03:52. A raccoon made contact with the conductor by climbing on top of the 44KV Aux breaker causing the 44KV Yellow Bus differential relay 87BG to operate. Service to all affected 44KV lines was restored by 05:18. This outage affected the following circuits : Gatewood Ret, Monroeton Ret, Ruffin Ret ~~~ 5/9/2019 ¦ gla4211 ¦ Investigative Action
10 | Sub/T | Reidsville gla4211 | RUFFIN - 17021203 | 5/8/2019 03:52 | 5/8/2019 05:17 | 11208419 | S-CKT - ABC Size: Class 3 FID: 38358333 | 11 Transmission device | 11 Transmission | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J8 Raccoon |  | F2 Forced Outage | 00 Calm | 910 | 916 | 85 | Sadler Tie | ECC TECH BRIAN PIERCY 336-823-1454 RESPONDING - TRANSMISSION OUTAGE - MEADOW SUMMIT 1 & 2, RUFFIN AND VANGAURD 45KV LINES ARE OUT - ECC INVESTIGATING - RACCOON GOT ON 44KV BUS INSIDE SWITCHING STATION CAUSING ALL FOUR TRANSMISSION LINES TO LOCKOUT | G Akers .. Comments from Joe Lambeth. ÂÂThe Sadler Tie 44KV Yellow Bus experienced an interruption this morning at 03:52. A raccoon made contact with the conductor by climbing on top of the 44KV Aux breaker causing the 44KV Yellow Bus differential relay 87BG to operate. Service to all affected 44KV lines was restored by 05:18.ÂÂ This outage affected the following circuits : Gatewood Ret, Monroeton Ret, Ruffin Ret ~~~ 5/9/2019 ¦ gla4211 ¦ Investigative Action
11 | Sub/T | Reidsville gla4211 | RUFFIN - 17021201 | 5/8/2019 03:52 | 5/8/2019 05:17 | 11208417 | S-CKT - ABC Size: Class 3 FID: 38372221 | 11 Transmission device | 11 Transmission | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J8 Raccoon |  | F2 Forced Outage | 00 Calm | 568 | 568 | 85 | Sadler Tie | ECC TECH BRIAN PIERCY 336-823-1454 RESPONDING - TRANSMISSION OUTAGE - MEADOW SUMMIT 1 & 2, RUFFIN AND VANGAURD 45KV LINES ARE OUT - ECC INVESTIGATING - RACCOON GOT ON 44KV BUS INSIDE SWITCHING STATION CAUSING ALL FOUR TRANSMISSION LINES TO LOCKOUT | G Akers .. Comments from Joe Lambeth. ÂThe Sadler Tie 44KV Yellow Bus experienced an interruption this morning at 03:52. A raccoon made contact with the conductor by climbing on top of the 44KV Aux breaker causing the 44KV Yellow Bus differential relay 87BG to operate. Service to all affected 44KV lines was restored by 05:18. This outage affected the following circuits : Gatewood Ret, Monroeton Ret, Ruffin Ret. Cost of outage $300.00 ~~~ 5/9/2019 ¦ gla4211 ¦ Investigative Action
12 | Sub/T | Reidsville gla4211 | RUFFIN - 17021202 | 5/8/2019 03:52 | 5/8/2019 05:17 | 11208418 | S-CKT - ABC Size: Class 3 FID: 38358141 | 11 Transmission device | 11 Transmission | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J8 Raccoon |  | F2 Forced Outage | 00 Calm | 864 | 865 | 85 | Sadler Tie | ECC TECH BRIAN PIERCY 336-823-1454 RESPONDING - TRANSMISSION OUTAGE - MEADOW SUMMIT 1 & 2, RUFFIN AND VANGAURD 45KV LINES ARE OUT - ECC INVESTIGATING - RACCOON GOT ON 44KV BUS INSIDE SWITCHING STATION CAUSING ALL FOUR TRANSMISSION LINES TO LOCKOUT | G Akers .. Comments from Joe Lambeth. ÂThe Sadler Tie 44KV Yellow Bus experienced an interruption this morning at 03:52. A raccoon made contact with the conductor by climbing on top of the 44KV Aux breaker causing the 44KV Yellow Bus differential relay 87BG to operate. Service to all affected 44KV lines was restored by 05:18.Â This outage affected the following circuits : Gatewood Ret, Monroeton Ret, Ruffin Ret ~~~ 5/9/2019 ¦ gla4211 ¦ Investigative Action
13 | Sub/T | Reidsville gla4211 | MONROETON - 17121202 | 5/8/2019 03:53 | 5/8/2019 05:18 | 11208421 | S-CKT - ABC Size: Class 3 FID: 38371141 | 11 Transmission device | 11 Transmission | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J8 Raccoon |  | F2 Forced Outage | 00 Calm | 596 | 598 | 85 | Sadler Tie | ECC TECH BRIAN PIERCY 336-823-1454 RESPONDING - TRANSMISSION OUTAGE - MEADOW SUMMIT 1 & 2, RUFFIN AND VANGAURD 45KV LINES ARE OUT - ECC INVESTIGATING - RACCOON GOT ON 44KV BUS INSIDE SWITCHING STATION CAUSING ALL FOUR TRANSMISSION LINES TO LOCKOUT | G Akers .. Comments from Joe Lambeth. âThe Sadler Tie 44KV Yellow Bus experienced an interruption this morning at 03:52. A raccoon made contact with the conductor by climbing on top of the 44KV Aux breaker causing the 44KV Yellow Bus differential relay 87BG to operate. Service to all affected 44KV lines was restored by 05:18.â This outage affected the following circuits : Gatewood Ret, Monroeton Ret, Ruffin Ret ~~~ 5/9/2019 ¦ gla4211 ¦ Investigative Action
14 | Sub/T | Reidsville gla4211 | MONROETON - 17121201 | 5/8/2019 03:53 | 5/8/2019 05:18 | 11208420 | S-CKT - ABC Size: Class 3 FID: 38358177 | 11 Transmission device | 11 Transmission | 04 Wildlife | 04 Wildlife | 53 Restored Transmission/Sub Pow | NA | J8 Raccoon |  | F2 Forced Outage | 00 Calm | 736 | 735 | 85 | Sadler Tie | ECC TECH BRIAN PIERCY 336-823-1454 RESPONDING - TRANSMISSION OUTAGE - MEADOW SUMMIT 1 & 2, RUFFIN AND VANGAURD 45KV LINES ARE OUT - ECC INVESTIGATING - RACCOON GOT ON 44KV BUS INSIDE SWITCHING STATION CAUSING ALL FOUR TRANSMISSION LINES TO LOCKOUT | G Akers .. Comments from Joe Lambeth. "ÂThe Sadler Tie 44KV Yellow Bus experienced an interruption this morning at 03:52. A raccoon made contact with the conductor by climbing on top of the 44KV Aux breaker causing the 44KV Yellow Bus differential relay 87BG to operate. Service to all affected 44KV lines was restored by 05:18."Â This outage affected the following circuits : Gatewood Ret, Monroeton Ret, Ruffin Ret ~~~ 5/9/2019 ¦ gla4211 ¦ Investigative Action
15 | Sub/T | Eden gla4211 | LEAKSVILLE - 27100401 | 5/18/2019 00:00 | 5/18/2019 03:49 | 11217412 | S-CKT - ABC Size: Class 1A FID: 38359269 | 00 Substation device | 00 Substation | 05 Planned (IEEE) | 07 Proactive Work | 54 Scheduled | P1 Pole, Creosote |  |  | P2 Scheduled Outage | 00 Calm | 761 | 756 | 229 |  | ECC TECH MICHAEL HUTCHINSON 336-430-2819 PLANNED OUTAGE FOR TRANSMISSION - REBUILD IN LEAKSVILLE SUBSTAION -6 HR OUTAGE | G Akers .. transmission needed a planned outage for the rebuild of Leaksville substation. The transmission pole outside the substation needed to be replaced and required an outage to complete the work. ~~~ 5/20/2019 ¦ gla4211 ¦ Investigative Action
16 | Sub/T | Eden gla4211 | LEAKSVILLE - 27100402 | 5/18/2019 00:00 | 5/18/2019 03:50 | 11217414 | S-CKT - ABC Size: Class 1A FID: 38359305 | 00 Substation device | 00 Substation | 05 Planned (IEEE) | 07 Proactive Work | 54 Scheduled | P1 Pole, Creosote |  |  | P2 Scheduled Outage | 00 Calm | 612 | 615 | 230 |  | ECC TECH MICHAEL HUTCHINSON 336-430-2819 PLANNED OUTAGE FOR TRANSMISSION - REBUILD IN LEAKSVILLE SUBSTAION - 6 HR OUTAGE | G Akers .. transmission needed a planned outage for the rebuild of Leaksville substation. The transmission pole outside the substation needed to be replaced and required an outage to complete the work. ~~~ 5/20/2019 ¦ gla4211 ¦ Investigative Action
17 | Sub/T | Reidsville gla4211 | MONROETON - 17121202 | 5/26/2019 09:31 | 5/26/2019 13:34 | 11225916 | S-CKT - ABC Size: Class 3 FID: 38371141 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 46 Replaced Insulator | 38 Insulator | J3 Squirrel |  | F2 Forced Outage | 00 Calm | 596 | 598 | 243 | WILDLIFE CONTACT ON INSULATOR IN STATION | STATION OUTAG...ECC AWARE AND WILL DISPATCH TECH, ANIMAL CONTACT IN SUBSTATION DAMAGIN EQUIPMENT. CREW ON SITE TO MAKE REPAIRS SWITCHING OPTIONS BEING LOOKED AT. DUTY SUPERVISOR AWARE. REPAIRS MADE AS OF 1340 | G Akers .. squirrel caused damage to bus insulator. ~~~ 5/29/2019 ¦ gla4211 ¦ Investigative Action
18 | Sub/T | Reidsville gla4211 | MONROETON - 17121201 | 5/26/2019 09:31 | 5/26/2019 13:32 | 11225915 | S-CKT - ABC Size: Class 3 FID: 38358177 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 46 Replaced Insulator | 38 Insulator | J3 Squirrel |  | F2 Forced Outage | 00 Calm | 735 | 735 | 241 | WILDLIFE CONTACT ON INSULATOR IN STATION | STATION OUTAG...ECC AWARE AND WILL DISPATCH TECH, ANIMAL CONTACT IN SUBSTATION DAMAGIN EQUIPMENT. CREW ON SITE TO MAKE REPAIRS SWITCHING OPTIONS BEING LOOKED AT. DUTY SUPERVISOR AWARE..REPAIRS MADE AS OF 1340 | G Akers .. squirrel caused damage to bus insulator. Cost of outage was $3,500.00 ~~~ 5/29/2019 ¦ gla4211 ¦ Investigative Action
19 | Sub/T | LEWISVILLE sba8312 | HINSHAW BANK - 03151210 | 5/28/2019 10:11 | 5/28/2019 10:41 | 11227052 | S-CKT - ABC Size: Class 3 FID: 38373136 | 01 Feeder Breaker/Recl in Substa | 00 Substation | 04 Wildlife | 04 Wildlife | 14 Closed Breaker | BW Buswork | J3 Squirrel |  | F2 Forced Outage | 00 Calm | 1,170 | 1166 | 30 | inside fence @ Hinshaw Substation on ug buswork | LOCK OUT--LV522/WEANGEL ENROUTE - TECH FOUND DEAD SQUIRREL IN STATION NEAR 1210 BREAKER - TECH CLEARED IT UP - DCC CLOSED BREAKER, IT HELD | Crew found squirrel on ug bus work inside station/blew animal guard off/spoke with Jay Hundley about replacing/skh9815 ~~~ 5/29/2019 ¦ sba8312 ¦ Investigative Action
20 | Sub/T | Greensboro gla4211 | LAKE TOWNSEND RET - 09302408 | 5/31/2019 15:41 | 5/31/2019 17:15 | 11231153 | S-CKT - ABC Size: Class 3 FID: 38373176 | 11 Transmission device | 11 Transmission | EA Weather | TL Tree fails, NAC | 53 Restored Transmission/Sub Pow | NA | PP Yellow Poplar (tulip) | 91 | F2 Forced Outage | 03 Wind | 3,393 | 3398 | 94 | Span 42 Dan River White line | DAN RIVER 100KV TRANSMISSION OUTAGE - STRAIGHT- LINE WINDS GOT TOP PHASE AND MIDDLE PHASE TOGETHER ON 100 KV TRANSMISSION LINES LOCKING OUT | G Akers ..comments from Jericho Belcher Âa poplar tree uprooted during a high wind event and made contact with the white side of Dan River White. The conductors were wrapped around each other due to the contact. There was not apparent rot or weakness observed in the tree. The poplar was 107 feet tall and 91 feet from center. Multiple trees fell in span 42 and an oak leaning away from the line broke off about 45 feet above the ground and made contact with the lines as well. Multiple broken trees were observed.Â ~~~ 6/7/2019 ¦ gla4211 ¦ Investigative Action
21 | Sub/T | Greensboro gla4211 | LAKE TOWNSEND RET - 09302402 | 5/31/2019 15:41 | 5/31/2019 17:15 | 11231149 | S-CKT - ABC Size: Class 3 FID: 384600722 | 11 Transmission device | 11 Transmission | EA Weather | TL Tree fails, NAC | 53 Restored Transmission/Sub Pow | NA | PP Yellow Poplar (tulip) | 91 | F2 Forced Outage | 03 Wind | 1,623 | 1623 | 94 | Span 42 Dan River White line | DAN RIVER 100KV TRANSMISSION OUTAGE - STRAIGHT- LINE WINDS GOT TOP PHASE AND MIDDLE PHASE TOGETHER ON 100 KV TRANSMISSION LINES LOCKING OUT | G Akers ..comments from Jericho Belcher Âa poplar tree uprooted during a high wind event and made contact with the white side of Dan River White. The conductors were wrapped around each other due to the contact. There was not apparent rot or weakness observed in the tree. The poplar was 107 feet tall and 91 feet from center. Multiple trees fell in span 42 and an oak leaning away from the line broke off about 45 feet above the ground and made contact with the lines as well. Multiple broken trees were observed. ~~~ 6/7/2019 ¦ gla4211 ¦ Investigative Action
22 | Sub/T | Greensboro gla4211 | LAKE TOWNSEND RET - 09302407 | 5/31/2019 15:42 | 5/31/2019 17:15 | 11231155 | S-CKT - ABC Size: Class 3 FID: 38373166 | 11 Transmission device | 11 Transmission | EA Weather | TL Tree fails, NAC | 53 Restored Transmission/Sub Pow | NA | PP Yellow Poplar (tulip) | 91 | F2 Forced Outage | 03 Wind | 1,674 | 1675 | 93 | Span 42 Dan River White line | DAN RIVER 100KV TRANSMISSION OUTAGE - STRAIGHT- LINE WINDS GOT TOP PHASE AND MIDDLE PHASE TOGETHER ON 100 KV TRANSMISSION LINES LOCKING OUT | G Akers ..comments from Jericho Belcher a poplar tree uprooted during a high wind event and made contact with the white side of Dan River White. The conductors were wrapped around each other due to the contact. There was not apparent rot or weakness observed in the tree. The poplar was 107 feet tall and 91 feet from center. Multiple trees fell in span 42 and an oak leaning away from the line broke off about 45 feet above the ground and made contact with the lines as well. Multiple broken trees were observed. ~~~ 6/7/2019 ¦ gla4211 ¦ Investigative Action
23 | Sub/T | Greensboro gla4211 | LAKE TOWNSEND RET - 09302401 | 5/31/2019 15:42 | 5/31/2019 17:15 | 11231169 | S-CKT - ABC Size: Class 3 FID: 384600729 | 11 Transmission device | 11 Transmission | EA Weather | TL Tree fails, NAC | 53 Restored Transmission/Sub Pow | NA | PP Yellow Poplar (tulip) | 91 | F2 Forced Outage | 03 Wind | 1,325 | 1327 | 93 | Span 42 Dan River White line | DAN RIVER 100KV TRANSMISSION OUTAGE - STRAIGHT- LINE WINDS GOT TOP PHASE AND MIDDLE PHASE TOGETHER ON 100 KV TRANSMISSION LINES LOCKING OUT | G Akers .. straight line winds got top and middle phase conductor on Dan River 100 KV line together locking out the Dan River 100 KV line. ~~~ 6/7/2019 ¦ gla4211 ¦ Investigative Action
24 | Sub/T | Reidsville gla4211 | WENTWORTH - 17031206 | 5/31/2019 16:04 | 5/31/2019 17:56 | 11231425 | S-CKT - ABC Size: Class 1 FID: 366596171 | 11 Transmission device | 11 Transmission | EA Weather | TL Tree fails, NAC | 53 Restored Transmission/Sub Pow | NA | PP Yellow Poplar (tulip) | 91 | F2 Forced Outage | 03 Wind | 1,328 | 1327 | 112 | Span 42 Dan River White line | DAN RIVER 100KV TRANSMISSION OUTAGE - STRAIGHT- LINE WINDS GOT TOP PHASE AND MIDDLE PHASE TOGETHER ON 100 KV TRANSMISSION LINES LOCKING OUT | G Akers ..comments from Jericho Belcher a poplar tree uprooted during a high wind event and made contact with the white side of Dan River White. The conductors were wrapped around each other due to the contact. There was not apparent rot or weakness observed in the tree. The poplar was 107 feet tall and 91 feet from center. Multiple trees fell in span 42 and an oak leaning away from the line broke off about 45 feet above the ground and made contact with the lines as well. Multiple broken trees were observed. ~~~ 6/7/2019 ¦ gla4211 ¦ Investigative Action
25 | Sub/T | HIGH POINT FAPlumm | LINDEN ST SW STA - 10042412 | 6/7/2019 23:45 | 6/8/2019 00:43 | 11240214 | S-CKT - ABC Size: Class 2 FID: 38354841 | 00 Substation device | 00 Substation | 04 Wildlife | 04 Wildlife | 14 Closed Breaker | NA | J5 Snake |  | F2 Forced Outage | 02 Rain | 2,009 | 2009 | 58 | Linden St. Station bus work | GOT ON LOW SIDE BETWEEN THE BANKS IN SUBSTATION | faplumm...A snake made contact on the load break disconnect between banks 2 & 3. Transmission tech was able to remove the snake and re-energize the circuit. The estimated cost of the outage was $300.00. Pike ~~~ 6/10/2019 ¦ FAPlumm ¦ Investigative Action
26 | Sub/T - MED | Reidsville gla4211 | REIDSVILLE - 17010405 | 6/20/2019 14:12 | 6/20/2019 16:11 | 11256552 | S-CKT - ABC Size: Class 3 FID: 38358165 | 01 Feeder Breaker/Recl in Substa | 00 Substation | 28 Other Cause | 12 Lockout Without Perm Fault | 27 Other/See Notes | S9 Breaker |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 512 | 510 | 119 | unknown | CMPL 2019-06-20 16:11:00 by CBC4894 RMK: LOCKOUT WITH FAILURE TO CLOSE ALARM / TCC TECH ENROUTE @ 1417 / AB TARGETS 3146 FMAG, NO FMAX GIVEN / UNABLE TO DETERMINE POSSIBLE FAULT LOCATION...NO PROBLEM FOUND. SWITCHED TO AUX AND CLOSED BREAKER | PAUL MILLER TCC ENROUTE 336 314 1318 / BREAKER 0405 CLOSE COIL IS BURNT / WILL TEST AUX BUS AND WHEN DL IS READY TO TRY IT THE LOAD WILL BE MOVED TO AUX BREAKER G Akers .. There was no permanent fault on the line. This would have only been a momentary. ~~~ 6/25/2019 ¦ gla4211 ¦ Investigative Action
27 | Veg | Greensboro gla4211 | LAKE TOWNSEND RET - 09302407 | 4/5/2019 15:22 | 4/5/2019 17:47 | 11164930 | RCL - ABC Size: 200 4E FID: 166787641 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PV Pine, Virginia | 25 | F2 Forced Outage | 02 Rain | 569 | 1675 | 145 | 5074 Bass Chapel Rd | RELATED E# 11164946 | G Akers .. dead pine tree 25 feet from line split at ground and fell over into three phase line. This location is second span past recloser ~~~ 5/7/2019 (32 days) ¦ gla4211 ¦ Investigative Action
28 | Veg | LEWISVILLE skh9815 | HINSHAW BANK - 03151208 | 4/15/2019 00:53 | 4/15/2019 02:30 | 11175209 | S-RCL - ABC Size: 560 WVE FID: 39008763 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | LL Tree limb fails | DN No apparent defect | NA | BP Bradford Pear |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,745 | 2544 | 97 | 425 Brent Street | FAULT HALO'D AROUND FACID 39064853, SENECA ST, QUEEN ST, SUNSET DR/RCL LOCKOUT/FMAG 3579/B C TRIP/STORMS IN AREA/SLJ- RCL CLOSED IN | Crew found live Bradford pear limb across 2 phases @ 425 Brent St/crew removed limb and restored electronic/no damage to Duke equipment/issued WO 32482743 to change out pole and move middle phase to pole top on adjacent pole/ reqr skh9815 ~~~ 4/16/2019 ¦ skh9815 ¦ Work Order(s) Generated
29 | Veg - MED | Greensboro ELamb | PLEASNT GARD - 09791203 | 4/15/2019 16:04 | 4/15/2019 16:57 | 11176627 | S-CKT - ABC Size: Class 1A FID: 38357433 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | 29 Conductor, bare | OA Oak | 18 | F2 Forced Outage | 00 Calm | 970 | 966 | 53 | 6825 BRANSON MILL RD | CMPL 2019-04-15 17:03:00 by JRODR16 RMK: CKT LOCKED OUT ABC TARETS 2618 / POSS FAULT LOCATION ON BRANSON MILL RD BETWEEN GARDEN VALLEY CT AND HWY 62 E // 6825 BRANSON MILL RD / TREE ACROSS ALL 3 PHASES | ELamb: At 6825 Branson Mill RD, a Live Oak Tree Limb a distance of 18ft from the center line broke and fell on the middle and road phases causing the outage. Work order generated to change rotten poles, install crossarms, and change out flashed insulators. ~~~ 4/17/2019 ¦ ELamb ¦ Work Order(s) Generated
30 | Veg | Reidsville cag4361 | WENTWORTH - 17031212 | 4/18/2019 11:00 | 4/18/2019 12:36 | 11179405 | SOH - ABC Size: 600 Line Disconnect FID: 39078373 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | PV Pine, Virginia | 32 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,513 | 1720 | 96 | 3203 Ashley Loop Rd | CMPL 2019-04-18 12:59:00 by REPEOPL RMK: CIRCUIT LOCKOUT FMAG - BC T(50) 3704 - SUPV JIM LEWIS AWARE - TREE ON LINE/BRUSH FIRE - FD ON SCENE 3203 ASHLEY LOOP | cag4361 circuit locked out. See Event 11179347 for circuit outage. Out due to a dead Virginia pine tree 32ft off RW. Tree broke 3 ft off ground. No FUN ~~~ 4/23/2019 ¦ cag4361 ¦ Investigative Action
31 | Veg - MED | LEWISVILLE skh9815 | MT TABOR BNK - 03221208 | 4/19/2019 14:30 | 4/19/2019 23:43 | 11180853 | S-RCL - ABC Size: 560 WVE FID: 38996801 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | PT PINE |  | F2 Forced Outage | 17 Wind and Rain | 762 | 1760 | 553 | 5000 Gessner Place | LV373-KRA/LV522-WBJ-560 WVE OUT_Tree on line off Commonwealth swaim 4/19@720pm..LOCKOUT AFTER CLOSING TARGET AC FMAG 1940.......2ND LOCKOUT AFTER CLOSING TARGET AC FMAG 1961- PINE TREE WAS LAYING ON ALL 3 PHASES OUTSIDE OF R.O.W | Crew cut several trees from line and tried electronic/did not stay on/removed live pine limb across 2 phases @ 5000 Gessner Place/circuit being trimmed this spring/no fu reqr skh9815 ~~~ 4/23/2019 ¦ skh9815 ¦ Investigative Action
32 | Veg - MED | Chapel Hill rlw2159 | JAMES ST - 19031206 | 4/19/2019 16:08 | 4/20/2019 00:52 | 11181834 | RCL - ABC Size: 200 L FID: 39007375 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 29 Permanent Repair | CR Crossarm | HW HARDWOOD |  | F2 Forced Outage | 11 Tornado/Wind Shear/Microburst | 518 | 1759 | 524 | 1501 Dairyland | 200 L SOLAR SITE OUT | rlw2159-(TORNADO MED DAY) Poplar tree tore down 2 spans of #4 cu pri/neut and broke crossarm. ~~~ 4/22/2019 ¦ rlw2159 ¦ Completion Codes or Remarks
33 | Veg - MED | Chapel Hill rlw2159 | BINGHAM - 19251210 | 4/19/2019 16:17 | 4/20/2019 00:54 | 11183193 | SOH - ABC Size: 600 Line Disconnect FID: 39041118 | 08 Disconnect | OH Distribution Line Overhead | EA Weather | 03 Tree (Vegetation) | DA Damaged | 29 Conductor, bare | HW HARDWOOD | 30 | F2 Forced Outage | 11 Tornado/Wind Shear/Microburst | 1,591 | 1660 | 517 | HWY 70-A and Meadowland DR | CMPL 2019-04-20 00:50:00 by CRBARWI RMK: opened FAC ID 39041118 will Ground down lines then verify we can re energize station breaker, grounds hung at meadow land dr, found a broken insulator at tuscorora. Tornado caused trees to fall on line. Repairs mad | rlw2159-(MED DAY)broken insulator at tuscorora, also had 1 span of primary down and 6 broke insulators @ Meadowlands Dr & HWY 70A. Disconnects at FID# 39041118 were closed and circuit re-energized. Associated tickets are 11181938(blink), 11181954(circuit lockout) & 11183691(open circuit to close disconnects) ~~~ 4/22/2019 ¦ rlw2159 ¦ Investigative Action
34 | Veg - MED | Greensboro cag4361 | JESSUPTOWN - 09072414 | 4/19/2019 16:22 | 4/19/2019 20:10 | 11181972 | RCL - ABC Size: 200 4E FID: 38999165 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | CR Eastern Redcedar | 18 | F2 Forced Outage | 04 Wind, Rain and Lightning | 588 | 2917 | 228 | intersection of Wescott and Bunch Rd | 200 4E | cag4361 Recloser lockout due to cedar tree that fell at intersection of Wescott Dr and Bunch Rd. Tree was live and blew over. Ground has been wet for months and the high wind blew it over. Some Wire was still damaged at outage location so we got a crew to go repair. Outage was extended when reclosers were energized the road phase primary at the intersection of Northwest Sch Rd and Wallingford Rd burned down from cold load pickup. Wire was previously damaged by white pine tree. Crew Spliced wire and put all reclosers back on. Work Order generated to better isolate school and fire department from downstream trees ~~~ 4/23/2019 ¦ cag4361 ¦ Work Order(s) Generated
35 | Veg - MED | Greensboro gla4211 | SUMMERFIELD - 09102405 | 4/19/2019 16:31 | 4/19/2019 19:05 | 11182100 | S-CKT - ABC Size: Class 3 FID: 38374748 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | MP Maple | 21 | F2 Forced Outage | 17 Wind and Rain | 1,873 | 1880 | 154 | 4006 Oak Ridge Rd | 7507 SHADYSIDE DR, TREE REPORTED ON LINE SETZER/SMITH 334 WHITE-421 SHREVE 531 | G Akers .. limb from live mountain maple tree broke and fell across one circuit of double circuit line. Comment in crew remarks was for an outage behind a 50T fuse. ~~~ 5/2/2019 ¦ gla4211 ¦ Investigative Action
36 | Veg - MED | Greensboro ELamb | FERNWOOD - 09270403 | 4/19/2019 20:08 | 4/20/2019 18:41 | 11183238 | S-CKT - ABC Size: Class 3 FID: 38357769 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | EA Weather | TL Tree fails, NAC | DN No apparent defect | 30 Conductor, covered | OB Oak, white | 18 | F2 Forced Outage | 04 Wind, Rain and Lightning | 665 | 665 | 1353 | 2328 Fortune Lane | BREAKER OPENED DUE TO SEVERAL BROKE POLES JUST OUTSIDE THE STATION RELATED TO 11182148 SLC RLM 21:39 4/19 RELATED TO 11182148 SLC RLM 21:39 4/19 RELATED TO E#11183238 | ELamb: At 2328 Fortune Lane, a live white oak tree a distance of 18ft from the center line fell on the heavy wall primary breaking three pole: a pole with a transformer facility id 39545873, a poles with switches facility id 39038583, and the buck arm pole in back yard of 1305 N ELam Ave. When crew arrived primary was on the ground hot, so crew initiated circuit outage. No follow was needed. ~~~ 4/22/2019 ¦ ELamb ¦ Investigative Action
37 | Veg - MED | LEWISVILLE skh9815 | MAR-DON RET - 03211207 | 4/19/2019 20:41 | 4/19/2019 20:54 | 11183320 | S-CKT - ABC Size: Class 3 FID: 38375233 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | TF Tree fails, defective | DV Visible stem decay | P1 Pole, Creosote | MR Maple, red | 30 | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 1,958 | 2270 | 13 | 434 Vineyard Park Road | MOMENTARY DROP TO CUT JUMPERS DUE TO UNSAFE SITUATION. RELATED TO EVT 11181050 | Defective red maple with visible stem decay fell on neutral in last span before underground dip pole @ 434 Vineyard Park Road/tree was 30' from center of pole line/3 phase pole broken above neutral level/crew had circuit dropped in order to cut jumpers @ fac id 32982787 to isolate 3 phase tap/crew removed tree and changed out 40/5 pole, crossarm and oh tx//fu WO 32422914 to install 600amp disconnects on this tap for isolation/tap cannot be fused due to load/see 11180502 for jumper outage/count modified/skh9815 ~~~ 4/23/2019 ¦ skh9815 ¦ Work Order(s) Generated
38 | Veg | LEWISVILLE skh9815 | MAR-DON RET - 03211207 | 4/20/2019 03:24 | 4/20/2019 04:19 | 11183764 | S-CKT - ABC Size: Class 3 FID: 38375233 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | P1 Pole, Creosote | MR Maple, red | 30 | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 1,957 | 2270 | 55 | 434 VINEYARD PARK ROAD | DROPPED CIRCUIT FOR CREW TO SQUEEZE IN JUMPERS | Defective red maple with visible stem decay fell on neutral in last span before underground dip pole @ 434 Vineyard Park Road/tree was 30' from center of pole line/3 phase pole broken above neutral level/crew had circuit dropped in order to cut jumpers @ fac id 32982787 to isolate 3 phase tap/crew removed tree and changed out 40/5 pole, crossarm and oh tx//fu WO 32422914 to install 600amp disconnects on this tap for isolation/tap cannot be fused due to load/see 11180502 for jumper outage/count modified/this ticket for crews to make up jumpers/dropped OCB/skh9815 ~~~ 4/24/2019 ¦ skh9815 ¦ Work Order(s) Generated
39 | Veg | Eden gla4211 | RIDGEVIEW - 27111211 | 4/26/2019 13:00 | 4/26/2019 13:48 | 11190371 | S-CKT - ABC Size: Class 3 FID: 38359413 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | TL Tree fails, NAC | DD Co-dominate stem | 38 Insulator | PP Yellow Poplar (tulip) | 35 | F2 Forced Outage | 17 Wind and Rain | 854 | 1323 | 48 | BROKEN INSULATOR ON HARRINGTON HWY N OF HWY 87 | LOCKOUT TARGET AC FMAG 2389 FAULT HALO..ON HARRINGTON HWY FROM YOUNT RD TO LONGHOOK RD..ON ROBERTS RD FROM EDEN RD TO HWY 770..ON EDEN RD FROM 460 EDEN RD TO HEFFINGER RD..ON HWY 135 FROM TITAN BERRY RD TO 2600 NC HIGHWAY 135 | G Akers .. co-dominate stem of live tulip poplar tree 35 feet from line fell across three phase line. Pole top insulator broke. ~~~ 5/3/2019 ¦ gla4211 ¦ Investigative Action
40 | Veg - MED | ELKIN sba8312 | SMITHTOWN - 29081201 | 4/26/2019 16:11 | 4/26/2019 21:11 | 11192611 | S-RCL - ABC Size: 560 WVE FID: 39007297 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | C1 Crossarm, Creosote | OH Oak, water | 42 | F2 Forced Outage | 03 Wind | 502 | 1754 | 300 | NEBO and St John Rd | LOCKOUT TARGET AG FMAG 1074 TREE DOWN ST JOHNS RD/NEBO RD...TREE ON SITE ALSO.. TREE/LINE DOW | Defective Oak fell from O/S R/W breaking X-Arm and tearing down 2 Spans of Primary... Pics on R&I Server 20190426-11192611-Smithtown Ret. 29081201 ~~~ 4/28/2019 ¦ sba8312 ¦ Vegetation Management
41 | Veg - MED | HIGH POINT FAPlumm | RAGSDALE RET - 10192408 | 4/26/2019 17:26 | 4/26/2019 22:22 | 11194120 | RCL - ABC Size: 200 4E FID: 38998615 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | P1 Pole, Creosote | OA Oak | 60 | F2 Forced Outage | 17 Wind and Rain | 527 | 1563 | 296 | south of Southern Guilford High School on Wall Rd. | CMPL 2019-04-26 22:35:00 by BHORNE2 RMK: TREE ON LINES IN ROAD AND BROKE POLE fnw/4-26-19/2025/2 broke 40/5 poles-8' xarm thruline /10' fbg dbl de@ Southern Guilford HS | faplumm...A defective oak tree 60' from C/L of conductor with internal stem decay fell during a high wind event breaking two poles. Crew was able to sectionalize the outage and get the reclosers back on. I have created work order 32551286 to have a tree supervisor look at and remove a possible danger tree. Pic's on the R&I server. ~~~ 4/29/2019 ¦ FAPlumm ¦ Vegetation Management
42 | Veg - MED | RURAL HALL sba8312 | DANBURY RET - 03382403 | 4/26/2019 17:27 | 4/26/2019 23:45 | 11194211 | S-CKT - ABC Size: Class 3 FID: 38375381 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | 46 Replaced Insulator | 38 Insulator | MP Maple | 30 | F2 Forced Outage | 03 Wind | 760 | 764 | 378 | 1175 NC 8 & 89 | LOCKOUT..SCT CJACOB - 45' MAPLE ON LINE AT 1175 NC 8, POSSIBLE BAD 25KVA OHTX, POLE AND GUYS STILL LOOK OK. ADVISED UTILITY FOREMAN TRAVIS TRP INST 50 TARGET BC FMAG 1409 FAULT ON HC HWY 8 FROM STATION TO MOUNTAIN RD | Tree fall partial (maple) broke at fork of tree falling into 3 ph line and TX Crew C/O on set of DE bells, pole leaning will make job to C/ O pole. Rode circuit backbone out found a dead pine at edge of R/W that will need to be removed. ~~~ 4/29/2019 ¦ sba8312 ¦ Vegetation Management
43 | Veg - MED | LEWISVILLE lmh9203 | LEXINGTON - 03422408 | 4/26/2019 17:40 | 4/26/2019 23:01 | 11194614 | S-CKT - ABC Size: Class EX FID: 38350845 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DX Other defect | NA | EL Elm | 11 | F2 Forced Outage | 17 Wind and Rain | 919 | 923 | 321 | 601 MARKET ST | ON @ 2258_LOCKOUT. ALSO FEEDS WELCOME RET 1201 AND 1202 IN KERNERSVILLE - BACK ON - TREE FELL ON LINE AT W 5TH AND MARKET ST | AT 601 MARKET ST IN LEXINGTON, A LIVE LIMB FELL OUT OF AN ELM TREE 11' FROM THE CENTER LINE, WITH NO APPARENT DEFECT OTHER THAN IVY GROWING UP THE TREE. THE LIMB BROKE OUT OF THE TREE AND FELL ON TO THE PRIMARY LOCKING THE CIRCUIT OUT. THE CREW RODE THE LINE TO ASSURE NO OTHER DAMAGE ON THE LINE. THE EVENT WAS BACK PROPERTY AND WAS HARD TO PUT EYES ON BECAUSE IT WAS ON THE BACKSIDE OF THE TREE. NO DAMAGE TO LINES. CREW REMOVED LIMB AND PUT CIRCUIT BACK TO NORMAL....lmh ~~~ 4/30/2019 ¦ lmh9203 ¦ Investigative Action
44 | Veg - MED | KERNERSVILLE lmh9203 | WELCOME - 03391202 | 4/26/2019 17:40 | 4/26/2019 23:01 | 11194603 | S-CKT - ABC Size: Class 3 FID: 38351025 | 13 Distribution Source to Sub | 13 Distribution Source to Sub | 03 Vegetation | LL Tree limb fails | DX Other defect | NA | EL Elm | 11 | F2 Forced Outage | 17 Wind and Rain | 630 | 628 | 321 | 601 MARKET ST | FED BY LEXINGTON MAIN. LEXINGTON MAIN 2408 LOCKED OUT | RELATED TO E# 11194614....AT 601 MARKET ST IN LEXINGTON, A LIVE LIMB FELL OUT OF AN ELM TREE 11' FROM THE CENTER LINE, WITH NO APPARENT DEFECT OTHER THAN IVY GROWING UP THE TREE. THE LIMB BROKE OUT OF THE TREE AND FELL ON TO THE PRIMARY LOCKING THE CIRCUIT OUT. THE CREW RODE THE LINE TO ASSURE NO OTHER DAMAGE ON THE LINE. THE EVENT WAS BACK PROPERTY AND WAS HARD TO PUT EYES ON BECAUSE IT WAS ON THE BACKSIDE OF THE TREE. NO DAMAGE TO LINES. CREW REMOVED LIMB AND PUT CIRCUIT BACK TO NORMAL....lmh ~~~ 4/30/2019 ¦ lmh9203 ¦ Investigative Action
45 | Veg - MED | KERNERSVILLE lmh9203 | WELCOME - 03391201 | 4/26/2019 17:40 | 4/26/2019 23:02 | 11194602 | S-CKT - ABC Size: Class 3 FID: 38351001 | 13 Distribution Source to Sub | 13 Distribution Source to Sub | 03 Vegetation | LL Tree limb fails | DX Other defect | NA | EL Elm | 11 | F2 Forced Outage | 17 Wind and Rain | 999 | 999 | 322 | 601 MARKET ST | FED BY LEXINGTON MAIN. LEXINGTON MAIN 2408 LOCKED OUT | RELATED TO E# 11194614....AT 601 MARKET ST IN LEXINGTON, A LIVE LIMB FELL OUT OF AN ELM TREE 11' FROM THE CENTER LINE, WITH NO APPARENT DEFECT OTHER THAN IVY GROWING UP THE TREE. THE LIMB BROKE OUT OF THE TREE AND FELL ON TO THE PRIMARY LOCKING THE CIRCUIT OUT. THE CREW RODE THE LINE TO ASSURE NO OTHER DAMAGE ON THE LINE. THE EVENT WAS BACK PROPERTY AND WAS HARD TO PUT EYES ON BECAUSE IT WAS ON THE BACKSIDE OF THE TREE. NO DAMAGE TO LINES. CREW REMOVED LIMB AND PUT CIRCUIT BACK TO NORMAL....lmh ~~~ 4/30/2019 ¦ lmh9203 ¦ Investigative Action
46 | Veg - MED | LEWISVILLE skh9815 | MAR-DON RET - 03211203 | 4/26/2019 18:08 | 4/26/2019 19:45 | 11195033 | S-CKT - ABC Size: Class 3 FID: 38375239 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | LL Tree limb fails | DN No apparent defect | NA | MP Maple | 20 | F2 Forced Outage | 17 Wind and Rain | 2,474 | 2620 | 97 | 4800 Country Club Road | LOCKOUT TARGETG BG FMAG UNKNOWN | Large limb broken off from maple tree @ 4800 Country Club Road which fell on field circuit/slapped 2 phases on road circuit/no damage to Duke equipment/crew removed limb/no fu/skh9815 ~~~ 4/29/2019 ¦ skh9815 ¦ Investigative Action
47 | Veg | Chapel Hill rlw2159 | EASTGATE RET - 19021208 | 4/27/2019 18:35 | 4/27/2019 20:43 | 11197960 | S-CKT - ABC Size: Class 1 FID: 38359209 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | DE Erosion/poor enviornment | P1 Pole, Creosote | OA Oak | 25 | F2 Forced Outage | 03 Wind | 774 | 800 | 128 | 412 clayton tree on lines , broken pole. | CMPL 2019-04-27 22:01:00 by DKM3045 RMK: CKT LOCKOUT/FMAG 2968 A C TRIP 50/MOST LIKELY FAULT LOCATION NEAR FACID 38587733 OLD OXFORD AT MARKHAM DR - TREE REPORTED ON LINE AT 412 CLAYTON / ALSO AT 2020 MARKHAM | rlw2159 windy condition...large co dominate oak approximately 3" round at base,25' feet from center line fell due to wet area and defective base-- CKT LOCKOUT/FMAG 2968 A C TRIP 50/MOST LIKELY FAULT LOCATION NEAR FACID 38587733 OLD OXFORD AT MARKHAM DR - TREE REPORTED ON LINE AT 412 CLAYTON / ALSO AT 2020 MARKHAM..NEED FLAGGERS AND TREE CREW ON 417 CLAYTON RD Simmons, Michael (919) 437-9709 @7:58 called flaggers at 802***circuit out see 11197960 tree fell taking down primary lines breaking pole. crew cut jumpers to isolate see 11198066 and got circuit back on ...after repairs crew dropped circuit again see 11198298 to make jumpers back. ~~~ 4/29/2019 ¦ rlw2159 ¦ Investigative Action
48 | Veg | Chapel Hill rlw2159 | EASTGATE RET - 19021208 | 4/28/2019 05:04 | 4/28/2019 05:50 | 11198298 | S-CKT - ABC Size: Class 1 FID: 38359209 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | 14 Closed Breaker | P1 Pole, Creosote | OA Oak | 25 | P3 R Scheduled Outage | 03 Wind | 774 | 800 | 46 | 412 CLAYTON RD | DROPPED CIRCUIT TO MAKE UP JUMPERS - SEE EV11198066 | rlw2159-windy condition...large co dominate oak approximately 3" round at base, 25' feet from center line fell due to wet area and defective base-- CKT LOCKOUT/FMAG 2968 A C TRIP 50/MOST LIKELY FAULT LOCATION NEAR FACID 38587733 OLD OXFORD AT MARKHAM DR - TREE REPORTED ON LINE AT 412 CLAYTON / ALSO AT 2020 MARKHAM..NEED FLAGGERS AND TREE CREW ON 417 CLAYTON RD Simmons, Michael (919) 437-9709 @7:58 called flaggers at 802***circuit out see 11197960 tree fell taking down primary lines breaking pole. crew cut jumpers to isolate see 11198066 and got circuit back on ...after repairs crew dropped circuit again see 11198298 to make jumpers back. ~~~ 4/29/2019 ¦ rlw2159 ¦ Investigative Action
49 | Veg | Greensboro ELamb | STARMOUNT - 09720403 | 4/28/2019 18:50 | 4/28/2019 19:35 | 11198777 | S-CKT - ABC Size: Class 3 FID: 38356965 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | 30 Conductor, covered | PP Yellow Poplar (tulip) | 24 | P4 Crew Initiated Outage | 17 Wind and Rain | 506 | 506 | 45 | 3938 Starmount Dr | CMPL 2019-04-28 19:54:00 by DGFORRE RMK: GE518 Opened breaker to remove tree from primary at 3940 Starmount Dr for 15 minutes. Techs told us they would only need to drop circuit for 15 minutes | ELamb: Behind 3938 Starmount Dr, a yellow popular fell onto the heavy wall primary a distance of 24ft from the center line. with a defective of root rottens. According the crew the tree was downstream from a 100 T facility id but could not load break the 100 T because the cutouts did not have ear where that could hang the load breaking device. Therefore crew called for the circuit to be dropped so they could clear the tree off the primary. ~~~ 5/3/2019 ¦ ELamb ¦ Investigative Action
50 | Veg | MT AIRY sba8312 | TOAST - 28081205 | 5/2/2019 08:17 | 5/2/2019 08:39 | 11202111 | S-CKT - ABC Size: Class 3 FID: 38375125 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | B1 Brace | OR Oak, red | 60 | F2 Forced Outage | 00 Calm | 1,307 | 1331 | 22 | CORNER OF LYNN & WESTLAKE | CIRCUIT LOCK OUT DUE TO LIVE OAK TREE DAMAGE AT CORNER OF LYNN & WESTLAKE. OPENED SOLID BAR 39029003 TO ISOLATE. JOSH CHILDRESS MA41 | Defective red Oak fell 60' from line Breaking the X-arm braces and breaking tie wires. Crew isolated damage by opening disconnects ( event 11202134 ) and energizing Circuit. There is a job scoped to add a ELEC RCL and extend toast 1205 to sectionalize this tap to minimize exposure to the entire circuit...PICS on R&I Server 20190502-11202111-Toast Ret 28081205 ~~~ 5/3/2019 ¦ sba8312 ¦ Investigative Action
51 | Veg | LEWISVILLE pmb4141 | TURNERSBURG RET - 03651202 | 5/5/2019 02:46 | 5/5/2019 05:29 | 11205378 | S-CKT - ABC Size: Class 1A FID: 38350989 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | NA | PP Yellow Poplar (tulip) |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,067 | 1066 | 163 | 2421 Turnersburg Hwy | CMPL 2019-05-05 05:39:00 by KRA2897 RMK: LOCKOUT/TARGETS A-C/FMAG 1825 | A limb from an large overhanging poplar tree in the back yard fell across the 3 phase primary during a high wind event and locked out the circuit. Limb was gone by Monday. Pictures in folder. ~~~ 5/7/2019 ¦ pmb4141 ¦ Investigative Action
52 | Veg | LEWISVILLE skh9815 | PFAFFTOWN RET - 03271203 | 5/7/2019 21:01 | 5/7/2019 22:51 | 11208303 | S-CKT - ABC Size: Class 3 FID: 38376262 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LR Tree limb, dead, overhang | D2 Dead | NA | PP Yellow Poplar (tulip) |  | F2 Forced Outage | 17 Wind and Rain | 1,028 | 1031 | 110 | LEWISVILLE VIENNA RD @ OLDE FIELDS WAY | CMPL 2019-05-07 23:03:00 by ADBICKF RMK: RH C/O CKT LOCKOUT - AC TRIP - FMAG 2919 POSSIBLE FAULT LOCATION LEWISVILLE VIENNA RD & YADKINVIL NEAR DEVICE ID 39088971 | DEAD POPLAR LIMB FELL FROM OVERHANG ON LEWISVILLE VIENNA ROAD IN SPAN ACROSS FROM OLDE FIELDS WAY/LIMB ACROSS 2 PHASES/NO DAMAGE TO DUKE EQUIPMENT/FU 32571604 TO INSTALL 100T'S ON UNFUSED TAP OFF BACKBONE ON POLE ADJACENT TO OUTAGE LOCATION/SKH9815 ~~~ 5/8/2019 ¦ skh9815 ¦ Work Order(s) Generated
53 | Veg | KERNERSVILLE lmh9203 | BECKERDITE - 03021202 | 5/10/2019 09:14 | 5/10/2019 10:46 | 11210305 | S-CKT - ABC Size: Class EX FID: 38349729 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | DC Internal stem decay | P1 Pole, Creosote | EL Elm | 28 | F2 Forced Outage | 00 Calm | 963 | 962 | 92 | 4741 S MAIN ST | LOCKOUT...AG TARGETS. 3154 FMAG...AUTO TRIGGERED AT S MAIN AND HWY 52 FOR 1201...TREE BROKE POLE AT 4751 S MAIN ST...LINES GALLOPED TO LOCKOUT 1201 AND 1202 | AT 4741 S. MAIN ST, A PARTIAL ELM TREE WITH INTERNAL STEM DECAY, 28' FROM CENTER LINE, BROKE OFF INTO THE OH PRIMARY. THE FIELD PHASE AND NEUTRAL BROKE ALONG WITH 2 POLES. POLES AND WIRE FELL CAUSING THE CONDUCTOR TO GALLOP, PER CREW, TRIPPING 1201 AND 1202 AT THE STATION. ~~~ 5/14/2019 ¦ lmh9203 ¦ Investigative Action
54 | Veg | ELKIN pmb4141 | FALL CREEK - 29051202 | 5/11/2019 17:16 | 5/11/2019 22:48 | 11211521 | S-CKT - ABC Size: Class 3 FID: 38351157 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | PP Pole | OR Oak, red | 70 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,087 | 1087 | 332 | P3OH: 33324654-Past Wayne Farms/Finneys Poultry | CIRCUIT LOCKOUT - AG T(50) 3480....tree on line P3OH: 33324654...switching was available but was not used per field techs | A live red oak tree outside the R/W fell across Center Road and broke a 40' pole and the neutral, 1/2 mile from the station. Flaggers called at 17:45 and additional crews were called (from Mt. Airy and N. Wilkesboro). Grid told the crew they would verify that the breaker would carry load and check on possible switching. The crew removed the tree off the pole. When grid called the crew back, the switching procedure was still not completed and the crew stated they could change out the pole in about 1 1/2 hours which they felt would be quicker than switching due to the road still blocked by the NCDOT crews cleaning up the tree. Pics in folder. pmb ~~~ 5/13/2019 ¦ pmb4141 ¦ Investigative Action
55 | Veg | MT AIRY sba8312 | BANNERTOWN - 28061207 | 5/12/2019 22:43 | 5/13/2019 01:49 | 11212960 | S-RCL - ABC Size: 800 VPSS FID: 392365275 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | DC Internal stem decay | 29 Conductor, bare | OR Oak, red | 45 | F2 Forced Outage | 00 Calm | 602 | 1158 | 186 | 1894 reeves mill rd | CMPL 2019-05-13 01:52:00 by ADF4748 RMK: lockout targets CG FMAG 1143 | Tree fall partial top of Red Oak fell from 45' from line tearing down field and middle phases there was some wind gusts thru the night...Pics on R&I Server 20190512-11212960-Bannertown Ret 28061207 ..crew did not want to cut jumpers or isolate fault ~~~ 5/14/2019 ¦ sba8312 ¦ Investigative Action
56 | Veg | LEWISVILLE skh9815 | MAR-DON RET - 03211207 | 5/13/2019 08:25 | 5/13/2019 13:16 | 11213130 | RCL - ABC Size: 200 V4L FID: 39009700 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | DX Other defect | 29 Conductor, bare | LC Locust, Black | 40 | F2 Forced Outage | 00 Calm | 696 | 2270 | 291 | 4742 Country Club Road | CMPL 2019-05-13 13:15:00 by ABJAMES RMK: WIRE DOWN @ P3OH: 32988206 SEDGEFIELD PL & COUNTRY CLUB RD DUE TO TREE | Top of black locust tree covered with wisteria vines fell on double circuit pole line @ 4742 Country Club Road/road phase of field circuit 336 wire broken/crew removed tree and spliced wire back together/also blew lid from recloser protecting this line 2 spans upstream/FU WO 32695579 to take out 2 danger trees at this location/C&M supv issued emergency work order to replace 220V4L/crew had to drop adjacent circuit to get back back up/see event 11213501 for Mar-don 1203 outage/skh9815 ~~~ 5/14/2019 ¦ skh9815 ¦ Vegetation Management
57 | Veg | LEWISVILLE skh9815 | MAR-DON RET - 03211203 | 5/13/2019 12:20 | 5/13/2019 13:23 | 11213501 | S-CKT - ABC Size: Class 3 FID: 38375239 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | DX Other defect | 29 Conductor, bare | LC Locust, Black | 40 | F2 Forced Outage | 00 Calm | 2,616 | 2620 | 63 | 4742 Country Club Road | CMPL 2019-05-13 13:24:00 by ABJAMES RMK: open to allow crew to pull wire up on Mar -Don 1207 .. off for 1 hour to tie in wire. TREE FELL @ SEDGEFIELD PL & COUNTRY CLUB RD | Top of black locust tree covered with wisteria vines fell on double circuit pole line @ 4742 Country Club Road/road phase of field circuit 336 wire broken/crew removed tree and spliced wire back together/also blew lid from recloser protecting this line 2 spans upstream/FU WO 32695579 to take out 2 danger trees at this location/C&M supv issued emergency work order to replace 220V4L/crew had to Mar-don 1203 circuit to get back up/see event 11213130 for 200V4L outage on Mar-don 1207 outage/skh9815 ~~~ 5/14/2019 ¦ skh9815 ¦ Vegetation Management
58 | Veg | LEWISVILLE lmh9203 | CLEMMONS BK - 03071205 | 5/13/2019 16:25 | 5/13/2019 17:21 | 11213867 | S-CKT - ABC Size: Class 3 FID: 38349465 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | NA | OA Oak | 2 | F2 Forced Outage | 00 Calm | 1,540 | 1535 | 56 | 4000 Hampton Rd | LOCKOUT...TREE ON LINE AT 4000 HAMPTON. TECH REMOVED LIMB. STATION STALE. MANUAL OPERATION | AT 4000 HAMPTON RD, A LIMB FELL OUT OF AN OVER HANGING OAK TREE, ON TO THE 3-ph LOCKING THE CIRCUIT OUT. NO DAMAGE TO THE LINES. CREW REMOVED LIMB AND PUT THE CIRCUIT BACK TO NORMAL....WO#33180926 TO BRING 2 POLES UP TO STANDARDS TO FOR BETTER BIL..... lmh ~~~ 5/15/2019 ¦ lmh9203 ¦ Work Order(s) Generated
59 | Veg | KERNERSVILLE lmh9203 | CASSELL ST - 03061209 | 5/23/2019 06:34 | 5/23/2019 09:08 | 11221448 | S-CKT - ABC Size: Class 3 FID: 38375600 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | HT Tie, hand | CR Eastern Redcedar | 7 | F2 Forced Outage | 00 Calm | 1,838 | 1836 | 154 | 901 CASSELL ST | LOCK OUT...TARGETS ABC & FMAG 871 / halo at rosie and cassel. span of wire down at 901 cassell 35-45 MIN EST RESTORATION AT 0830.....8:20 operator tried reaching crews multiple times by phone and radio to ask about switching. Then called duty supv. PER SUPV DANNY GRAVLEY 336-406-7595 DOESNT WANT TO SWITCH DUE TO TIME TO RESTORE | AT 901 CASSELL ST, A RED CEDAR WITH ROOT ROT, 7' FROM THE CENTER LINE, FELL AND TORE A SPAN OF WIRE DOWN, ON FIELD PHASE, OFF INSULATOR.. CREW RE-TIED WIRE AND PUT CIRCUIT BACK TO NORMAL...lmh ~~~ 5/29/2019 ¦ lmh9203 ¦ Investigative Action
60 | Veg | LEWISVILLE skh9815 | MT TABOR BNK - 03221209 | 5/28/2019 12:15 | 5/28/2019 12:24 | 11227232 | S-CKT - ABC Size: Class 3 FID: 38350293 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DC Internal stem decay | NA | OA Oak | 20 | P4 Crew Initiated Outage | 00 Calm | 1,195 | 1193 | 9 | INTERSECTION OF FRIAR TUCK & HUNTINGDON | EMERGENCY DROP TO REMOVE TREE OFF PRIMARY...RELATED TO 1021 N PEACE HAVEN 11227123 | LARGE LIMB FROM OAK TREE BROKEN OFF AND FELL ACROSS 3 PHASE LINE ON FRIAR TUCK @ HUNTINGDON RD/CREW ATTEMPTED TO REMOVE TREE BUT WAS UNABLE TO SAFELY/ASKED FOR GRID TO DROP CIRCUIT/NO FU SKH9815 ~~~ 5/29/2019 ¦ skh9815 ¦ Investigative Action
61 | Veg | ELKIN sba8312 | YADKINVILLE - 29061207 | 5/29/2019 14:45 | 5/29/2019 15:21 | 11228666 | S-CKT - ABC Size: Class 1A FID: 38348951 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect | NA | PW Pine, white | 8 | F2 Forced Outage | 00 Calm | 873 | 875 | 36 | 733 E MAIN ST TREE IN ROW | LCKOUT..TARGETS INST 50 B TO C..FMAG 3710..KENT SUDDRETH DUTY SUPV AWARE | White Pine overgrown limb burned and fell across phases no wire down, crew cut tree limbs back and restored OCB .... Pics on R&I Server 20190529-11228666-Yadkinville Ret 29061207 This Circuit is on the TTM for 2019 to be started by the end of July 2019 HALOED ON US HWY 421 FROM HAYES RD FCID 38406268 TO FCID 38406274 AT MYERS RD AND ALSO DOWN FRED HINSHAW TO TRANSMISSION CROSSING ~~~ 5/30/2019 ¦ sba8312 ¦ Investigative Action
62 | Veg | Eden gla4211 | RIDGEVIEW - 27111211 | 5/29/2019 19:19 | 5/29/2019 20:49 | 11229027 | S-CKT - ABC Size: Class 3 FID: 38359413 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | SZ Sweet Gum | 18 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,325 | 1323 | 90 | Harrington hwy beside church of god in row | CMPL 2019-05-29 20:50:00 by MCOOKE2 RMK: Trees on line in 2 locations | G Akers .. live sweet gum tree 18 feet from the line twisted and broke 12 feet from the ground an fell into three phase primary. No damage to conductor. ~~~ 5/31/2019 ¦ gla4211 ¦ Investigative Action
63 | Veg | Greensboro ELamb | KILDARE - 09082405 | 5/30/2019 15:44 | 5/30/2019 16:33 | 11230169 | S-RCL - XZ Size: 800 VPSS FID: 384381716 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | LL Tree limb fails | DN No apparent defect | 29 Conductor, bare | SZ Sweet Gum | 36 | F2 Forced Outage | 00 Calm | 550 | 1690 | 49 | 1089 Knox Rd | related to event 11230140, | ELamb: At 1089 Knox Rd, a live limb of a sweetgum tree a distance of 36ft from the center line fell on the b phase causing the B phase to lockout on the upstream recloser facility id 384381716 for event 11229990. Due to the fire on the ground the remaining two phase of recloser 384381716 were dropped for event #11230169. Crew where able to open switch facility id 395017706 for event #11230140 to restoring 963 customers. ~~~ 6/25/2019 (26 days) ¦ ELamb ¦ Investigative Action
64 | Veg | Greensboro ELamb | KILDARE - 09082410 | 5/30/2019 16:43 | 5/30/2019 18:15 | 112301533 | S-CKT - ABC Size: Class 2 FID: 38356941 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | MR Maple, red | 36 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,839 Cust Eq: 837 | 3209 | 92 | 802 Willard St | CMPL 2019-05-30 19:04:00 by DGFORRE RMK: LOCKOUT..TARGET BC FMAG 4317 FAULT ON E WENDOVER AVE FROM ELWELL AVE TO N ENGLISH ST line down at intersection of Waugh St and E wendover Ave, near fac id 39492289 | ELamb: A dead maple tree at 802 Willard ST fell a distance of 36ft from the center and lockout the circuit. The open point recloser facility 396748893 that ties Kildare 09082410 with Kildare 09082412 closed in see event #112301531 to restore 837 customers up to recloser facility id 38998999 see event #112301532 because of automation. Dead maple tree was removed and power was restored. ~~~ 5/31/2019 ¦ ELamb ¦ Investigative Action
65 | Veg | Reidsville gla4211 | WENTWORTH - 17031212 | 5/31/2019 15:40 | 6/1/2019 11:45 | 11232801 | SOH - ABC Size: 600 Line Disconnect FID: 39078373 | 08 Disconnect | OH Distribution Line Overhead | EA Weather | TL Tree fails, NAC | 42 Replaced Crossarm/Brace | C1 Crossarm, Creosote | PV Pine, Virginia | 35 | F2 Forced Outage | 04 Wind, Rain and Lightning | 854 | 1720 | 1205 | Multiple locations on Ashley Loop Rd | solids restored and outage damaged further isolated | G Akers .. outage occurred on 100 KV line feeding Wentworth substation. Further damage on Wentworth 1212 circuit from downed trees during storm. These solid blades were pulled to allow circuit to be restored. See event # 11231152 for circuit outage. ~~~ 6/11/2019 ¦ gla4211 ¦ Investigative Action
66 | Veg | Greensboro ELamb | MERRITT DRVE - 09242405 | 5/31/2019 18:36 | 5/31/2019 19:33 | 11232184 | S-CKT - ABC Size: Class 2 FID: 38356713 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | LD Tree limb, dead | D2 Dead | 29 Conductor, bare | PP Yellow Poplar (tulip) | 15 | F2 Forced Outage | 17 Wind and Rain | 2,107 | 2109 | 57 | Across from 2901 Spring Garden St | CMPL 2019-05-31 19:37:00 by SMCOLL4 RMK: Circuit outage FMAG 802 Targets ABG, TX on fire fac id 40268312 MASONIC DR & SPRING GARDEN ST. dead tree limb fell across circuit | ELamb: Across from 2901 Spring Garden St, a dead limb of a yellow broke off a distance of 15ft from the center line and fell on the primary causing the outage. Created WO 33056840 to cause danger tree outside of ROW that could impact a double circuit line an WO to cut an overhanging limb that could fall on the double circuit tree is also outside the ROW ~~~ 6/4/2019 ¦ ELamb ¦ Work Order(s) Generated
67 | Veg | LEWISVILLE lmh9203 | SWAIMTOWN - 03321201 | 6/5/2019 15:42 | 6/5/2019 16:31 | 11236914 | S-CKT - ABC Size: Class 2 FID: 38350281 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect | NA | PC Pecan | 15 | F2 Forced Outage | 02 Rain | 2,139 | 2137 | 49 | 1731 BREWER RD | CKT LOCKOUT - AB FAULT - FMAG 1190. TREE ON LINE NEAR brewer st and linger st | AT 1731 BREWER RD, AN OVERGROWN ELM TREE WAS LAYING ON THE 3PH PRIMARY DUE TO LIMBS WEIGHTED DOWN BY THE RAIN. CREW WAS ABLE TO CUT OFF THE ENCROACHING LIMBS AND PUT THE CIRCUIT BACK TO NORMAL....NO DAMAGE...WILL HAVE VEG MGT LOOK AT REMOVING A POTENTIAL HAZARD TREE ON WO#33180709 ....lmh ~~~ 6/6/2019 ¦ lmh9203 ¦ Vegetation Management
68 | Veg | Burlington jhp2990 | TROLLINGWOOD - 11082414 | 6/6/2019 14:41 | 6/6/2019 17:43 | 11237798 | S-CKT - ABC Size: Class 2 FID: 38357997 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | 37 Removed Limb or Tree From Lin | 38 Insulator | A1 ABB | 2 | F2 Forced Outage | 00 Calm | 1,617 | 2026 | 182 | 445 GIBSON RD | LOCKOUT TARGETS 51 A TO C..FMAG 2852...TCC CONTACTED TECH ENROUTE 14:55, ALL OK IN STATION. CREW FOUND TREE LIMB ON TWO PHASES AT 445 GIBSON RD, ALSO HAD TO REPLACE DAMAGED INSULATOR AT SAME LOCATION. TALLEY, CAISON, BLEVINS, RILEY, CAMPBELL | AFTER INITIAL OUTAGE, NO FAULT WAS FOUND. CLOSED BREAKER WHILE BLOCKED BUT LOCKED OUT AGAIN. OPENED RECLOSER 39006138 TO ISOLATE AND CLOSED AGAIN BLOCKED BUT STILL LOCKED OUT. CREW FOUND LIMB ON TWO PHASES AT 445 GIBSON RD AND ALSO HAD TO REPLACE DAMAGED INSULATOR. LEFT RECLOSER 39006138 EVENT 11238021 OPENED DUE FOUND DAMAGED SMU FUSE AT FACID: 38564081 WHILE LOOKING FOR FAULT. ~~~ 6/7/2019 ¦ jhp2990 ¦ Investigative Action
69 | Veg | Greensboro cag4361 | RANDOLPH - 09042407 | 6/6/2019 19:09 | 6/6/2019 20:52 | 11238130 | S-RCL - ABC Size: 800 VPST FID: 39006744 | 02 Line Recloser | OH Distribution Line Overhead | 19 Lightning strike | LD Tree limb, dead | D2 Dead |  | OW Oak, willow | 13 | F2 Forced Outage | 05 Lightning | 1,632 | 4203 | 103 | 902 s Josephine Boyd st | NO COMMS WITH RCL / POSSIBE RCL OUTAGE - SHT0050 RECONFIGURED -PHALL/JGOODWIN ROAD RECLOSER TO OPEN POINT AT W GATE CITY BLVD/S AYCOCK/FOUND NOTHING/MAUALLY BLOCKED AND TRIED - HELD; TECHS STATED SMALL STORM WITH LIGHTING CAME THRU AREA MAY HAVE BEEN CAUS | Dead Tree limb on Willow Oak in front yard. Crew did not see limb on ride out and reenergized line. Original cause was lightning but changed to dead limb. Circuit went back out the next day see event 11239271 for next recloser lockout on 6-07-19 ~~~ 6/11/2019 ¦ cag4361 ¦ Investigative Action
70 | Veg | Greensboro cag4361 | RANDOLPH - 09042407 | 6/7/2019 14:41 | 6/7/2019 15:27 | 11239271 | S-RCL - ABC Size: 800 VPST FID: 39006744 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | D2 Dead |  | OW Oak, willow | 13 | F2 Forced Outage | 02 Rain | 1,632 | 4203 | 46 | 902 S Josephine Boyd | 3 PHSE LOCK OUT - TREE LIMB ON AYCOCK AND HAYWOOD ACROSS ONE PHASE GE344 WATSON/T WILLIAMS GE310 NORRIS | Dead tree limb on Willow oak. Tree limb fell on primary and had been laying on the primary for a while. This circuit had locked out previous but crew did not see and re-energized. See event 11238130 for previous lock out. Tree limb broken off by crew and closed recloser. Wire is ok and no follow up needed ~~~ 6/11/2019 ¦ cag4361 ¦ Investigative Action
71 | Veg | Greensboro cag4361 | RANDOLPH - 09042411 | 6/7/2019 21:49 | 6/8/2019 02:59 | 11240050 | S-CKT - ABC Size: Class 2 FID: 38374490 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead |  | AS Ash | 17 | F2 Forced Outage | 02 Rain | 1,077 | 1075 | 310 | DEAD TREE LIMB ON FLORIDA ST - 100 FT WEST F ALICE | LOUD BOOM @ 2207 DINSMORE ST & ARCING TX @ 1603 ALICE AVE & LOUD EXPLOSION @ 2105 E FLORIDA ST | dead limb on ash tree fell on primary. This tree was damaged from 2018 tornado. Crew cut back limbs. Primary pitted but ok ~~~ 6/11/2019 ¦ cag4361 ¦ Investigative Action
72 | Veg | Greensboro ELamb | JESSUPTOWN - 09072407 | 6/8/2019 00:27 | 6/8/2019 19:52 | 11240304 | RCL - ABC Size: 200 4E FID: 395374526 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | 29 Conductor, bare | SY Sycamore | 36 | F2 Forced Outage | 17 Wind and Rain | 506 | 3382 | 1165 | Across from 2503 Regents Park LN | REGENTS PARK - TR ON BLUFF RUN DRIVE - 2ND POLE - BUCK ARM POLE OK - NEEDS (1) 10FT FIBER, (2) REG WOOD 8'S, 2 POLE TOPS, 6 P&I NEED PADDLEFOOT TREE CREW AND (2) 4WD MHB'S - 1 HAND COIL 1/0 WIRE PADDLE TREE/2 4WD MHB -4 SPANS OF WIRE DOWN. PER CASEY CAIN , TORE DOWN WIRE BEFORE SOLID BLADES . TREES no further isolation options / op center supv aware & engaged | Elamb: Across from 2503 Regents Park LN, a sycamore tree a distance 36ft from the center line with a defect of Erosion fell causing the outage. No follow up needed. ~~~ 6/13/2019 ¦ ELamb ¦ Investigative Action
73 | Veg | Greensboro ELamb | RAGSDALE - 09352403 | 6/8/2019 00:29 | 6/8/2019 05:02 | 11240319 | S-RCL - ABC Size: 800 NVST FID: 39005635 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | TF Tree fails, defective | DR Roots rotten/defective | 29 Conductor, bare | MR Maple, red | 67 | F2 Forced Outage | 17 Wind and Rain | 1,994 | 3856 | 273 | 5622 Watercrest Dr. | RECL LOCKOUT B C FAULT FMAG 1985 | ELamb: Beside 5622 Watercrest Dr, a red maple a distance of 67ft from the center line with a defective of rooten roots fell causing the outage. No follow up are needed. Self Healing did not occur on this outage because the fault location is between the recloser facility 39005635 that was off because of the outage and the open point that ties Ragsdale 09352403 and Fairfax 09032410 recloser facility id 30878384. ~~~ 6/12/2019 ¦ ELamb ¦ Investigative Action
74 | Veg | Greensboro ELamb | MERRITT DRVE - 09242406 | 6/8/2019 01:41 | 6/8/2019 04:08 | 112403762 | S-RCL - ABC Size: 800 VPST FID: 386060742 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | MR Maple, red | 18 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,204 Cust Eq: 579 | 2106 | 147 | 3602 Cascade Dr | CMPL 2019-06-08 04:18:00 by JSEDWA1 RMK: tree fell across 3 phases of oh primary and neutral...tree was across the street from 3602 Cascade Dr....according to DCC the self-healing isolated the area | Elamb: Across from 3602 Cascade Dr, a live red maple a distance of 18ft from the center line fell causing the outage. No follow up is needed. Self healing did occur when recloser facility 386060732 close in which was a normal open that tied Merritt Drive 2406 to Merritt Dr 2412 for event 112403761 and then closed in recloser 39004620 allowing 579 customers to be saved due to self healing. ~~~ 6/12/2019 ¦ ELamb ¦ Investigative Action
75 | Veg | LEWISVILLE lmh9203 | EBERT RD RET - 03081201 | 6/8/2019 02:07 | 6/8/2019 03:44 | 11240420 | S-CKT - ABC Size: Class 3 FID: 50347638 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LX Trees, overgrown primary | 14 Closed Breaker | NA | MP Maple | 7 | F2 Forced Outage | 02 Rain | 1,788 | 1791 | 97 | 4122 EBERT RD | Lockout - 50 inst trip target AC FMAG 5085- no cause found ECC tech checked inside station and everything was good | OVERGROWN TREE LIMBS ACROSS 2 CIRCUITS OUT OF EBERT RET.......no cause found ECC tech checked inside station and everything was good. Station put back to normal.....RELATED TO # 11240501 & 11240517....lmh ~~~ 6/10/2019 ¦ lmh9203 ¦ Work Order(s) Generated
76 | Veg | LEWISVILLE lmh9203 | EBERT RD RET - 03081201 | 6/8/2019 04:06 | 6/8/2019 04:29 | 11240501 | S-CKT - ABC Size: Class 3 FID: 50347638 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 14 Closed Breaker | NA | MP Maple | 7 | F2 Forced Outage | 02 Rain | 1,787 | 1791 | 23 | 4122 EBERT RD - OUTSIDE STATION | Lock out Inst 50 Trip Targets AC FMAG5050-tree on both circuits right outsid the station | ACROSS FROM EBERT RD SS, AT 4122 EBERT RD, AN OVERGOWN MAPLE TREE AND OAK TREE, WEIGHED HEAVY ACROSS BOTH CIRCUITS DURING A STEADY RAIN, CAUSING CIRCUIT 1201 TO LOCKOUT. THE CREW WAS ABLE TO TRIM ENOUGH LIMBS AWAY FROM THE CONDUCTORS TO PUT THE STATION CIRCUITS BACK TO NORMAL. WO# 33181553 CREATED TO TRIM TREES....lmh ~~~ 6/10/2019 ¦ lmh9203 ¦ Work Order(s) Generated
77 | Veg | LEWISVILLE lmh9203 | EBERT RD RET - 03081203 | 6/8/2019 04:19 | 6/8/2019 04:29 | 11240517 | S-CKT - ABC Size: Class 3 FID: 50347342 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 14 Closed Breaker | NA | MP Maple | 7 | P4 Crew Initiated Outage | 02 Rain | 1,899 | 1901 | 10 | 4122 EBERT RD - OUTSIDE STATION | Bkr opened to remove tree limbs from double ckt-tree on both circuits right outsid the station | ACROSS FROM EBERT RD SS, AT 4122 EBERT RD, AN OVERGOWN MAPLE TREE AND OAK TREE, WEIGHED HEAVY ACROSS BOTH CIRCUITS DURING A STEADY RAIN, CAUSING CIRCUIT 1201 TO LOCKOUT. CREW OPENED 1203 BREAKER TO SAFELY TRIM ENOUGH LIMBS AWAY FROM THE CONDUCTORS TO PUT THE STATION CIRCUITS BACK TO NORMAL. WO# 33181553 CREATED TO TRIM TREES....lmh ~~~ 6/10/2019 ¦ lmh9203 ¦ Investigative Action
78 | Veg | Eden gla4211 | RIDGEVIEW - 27111212 | 6/8/2019 07:42 | 6/8/2019 09:23 | 11240778 | S-RCL - ABC Size: 560 WVE FID: 39000081 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 56 Sectionalized/Restored Servic | P1 Pole, Creosote | OR Oak, red | 55 | F2 Forced Outage | 04 Wind, Rain and Lightning | 502 | 1789 | 101 | HWY 700 & NC 87 | LOCKOUT/TARGETS A-B-C/FMAG 1465...BROKEN POLE AND CROSS ARMS AT HWY 700 & NC 87. OPENED SOLID BARS 39070200 TO ISOLATE AND CLOSE RECLOSER. MIKE COOK & DOUG LEATH | G Akers .. large red oak uprooted and fell over during storm breaking pole, crossarm and wire. Tree was on Old Hwy 87 across from Ware St. Solid blade opened on event # 11240904 to get electronic recloser back on. ~~~ 6/21/2019 ¦ gla4211 ¦ Investigative Action
79 | Veg | LEWISVILLE skh9815 | MT TABOR BNK - 03221208 | 6/8/2019 19:56 | 6/9/2019 06:46 | 11242024 | S-CKT - ABC Size: Class 3 FID: 38350197 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | TF Tree fails, defective | DR Roots rotten/defective | C2 Crossarm, Penta | OB Oak, white | 75 | F2 Forced Outage | 02 Rain | 1,760 | 1760 | 650 | 3957 Huddington Court | Lockout 50 inst trip targets ABG FMAG5629-Most likely fault location on Huddinton rd right outside the station-3966 Huddington Ct--several broken cross arms, lines down due to trees-tree crew enroute as of 2130 | White oak 75' from center of pole line uprooted and fell on double circuit @ 3957 Huddington Court/broke 10' & 8' arm and damaged tx on pole and broke 10' arm on adjacent pole/2 spans of 336 wire down/tree crew removed tree from line/crew replaced tx,3 wood xarms,and put up wire/also hung 600amp switches per grid to do switching procedure which locked out Mt Tabor 1205 when attempted/see events 11242025 & 11242845/skh ~~~ 6/10/2019 ¦ skh9815 ¦ Investigative Action
80 | Veg | RURAL HALL skh9815 | MT TABOR BNK - 03221207 | 6/8/2019 19:56 | 6/9/2019 06:45 | 11242025 | S-CKT - ABC Size: Class 3 FID: 38350101 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | C2 Crossarm, Penta | OB Oak, white | 75 | F2 Forced Outage | 02 Rain | 1,080 | 1080 | 649 | 3957 Huddington Court Winston Salem | 3966 Huddington Ct--several broken cross arms, lines down due to trees-tree crew enroute as of 2130 | White oak 75' from center of pole line uprooted and fell on double circuit @ 3957 Huddington Court/broke 10' & 8' arm and damaged tx on pole and broke 10' arm on adjacent pole/2 spans of 336 wire down/tree crew removed tree from line/crew replaced tx,3 wood xarms,and put up wire/also hung 600amp switches per grid to do switching procedure which locked out Mt Tabor 1205 when attempted/see events 11242024/skh9815 ~~~ 6/10/2019 ¦ skh9815 ¦ Investigative Action
81 | Veg | LEWISVILLE lmh9203 | LEWISVILLE - 03201206 | 6/8/2019 22:06 | 6/9/2019 00:28 | 11242273 | S-CKT - ABC Size: Class 3 FID: 38350089 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | LX Trees, overgrown primary | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 02 Rain | 1,161 | 1529 | 142 | 7515 Grapevine Rd | Lock out 50 INst Trip tarets AC FMAG 4848 | AT 7515 GRAPEVINE RD, THE RAIN CAUSED THE OVERGROWN TREES TO LAY ON THE PRIMARY ONE SPAN BEYOND THE RECLOSERS. THE RECLOSER COULD NOT CLEAR, THEN THE CIRCUIT TRIPPED. THE CREW CLEARED SOME LIMBS AND RETURNED THE CIRCUIT TO NORMAL. THIS CIRCUIT IS SCHEDULED TO BE TRIMMED IN FALL OF 2019. (2 HURRICANE EVENTS, 1 ICE STORM EVENT AND THIS THUNDERSTORM RAIN EVENT)....lmh ~~~ 6/10/2019 ¦ lmh9203 ¦ Investigative Action
82 | Veg | HIGH POINT FAPlumm | RAGSDALE RET - 10192408 | 6/9/2019 04:04 | 6/9/2019 07:10 | 11242849 | RCL - ABC Size: 200 4E FID: 38998615 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | 29 Conductor, bare | PP Yellow Poplar (tulip) | 33 | F2 Forced Outage | 02 Rain | 582 | 1563 | 186 | 1437 Burnetts Chapel Road | RCL 200 4E OUT FID # 38998615....TREE FELL PULLED CENTER PHASE OUT...DMBROW2 RESTORED | faplumm...A defective poplar tree with internal stem decay 33' from C/L fell during a wind and rain event breaking the middle phase conductor off of the insulator. Crew was able to tie the conductor in and reenergize the reclosers. Work order 32974638 was created to remove the tree off of the guy wire and to inspect and remove two possible danger tree's. Pic's on R&I server. ~~~ 6/12/2019 ¦ FAPlumm ¦ Vegetation Management
83 | Veg | RURAL HALL skh9815 | SHATTALN BK - 03301212 | 6/9/2019 04:35 | 6/9/2019 06:19 | 11242888 | S-CKT - ABC Size: Class 3 FID: 38375167 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | LH Tree limb, overhang | DN No apparent defect | NA | OW Oak, willow |  | F2 Forced Outage | 02 Rain | 1,255 | 1258 | 104 | 2041 Independence Road | Lockout targets AC 50 Inst trip FMAG 4919-Independence Rd from Williamsburg to Bethania Station mismapped- | willow oak limbs overhanging double circuit pole line weighted down from heavy rains on 2 phases @ 2041 Independence Road/crew cut limbs from primary and restored OCB/no damage to Duke equipment/circuit to be trimmed in 2019/no fu reqr skh9815 ~~~ 6/10/2019 ¦ skh9815 ¦ Investigative Action
84 | Veg | MT AIRY sba8312 | BANNERTOWN - 28061207 | 6/16/2019 19:52 | 6/17/2019 00:08 | 11251600 | SUG - ABC Size: 600 Line Disconnect FID: 406178211 | 10 Sectionalizer | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | 29 Conductor, bare | CH Black Cherry (Wild) | 30 | F2 Forced Outage | 00 Calm | 582 | 1158 | 256 | P3OH: 406178182 | CMPL 2019-06-17 00:10:00 by JFCHILD RMK: LINES DOWN AT P3OH: 406178182 DUE TO TREES - CREWS ISOLATED TO SWITCHES GOT RCL BACK ON - ONSITE MAKING REPAIRS - | Defective Cherry fell tearing down Field and Middle phase due to poor root system and vines, hard access issues crew had to cut fence to get to wire across creek. Anchor pulled up approx. 18".Will need to install a swamp anchor and try to straighten poles. Pics on R&I Server 20190616-11251600-Bannertown Ret 28061207. WO# 33047982 to install swamp anchor ~~~ 6/19/2019 ¦ sba8312 ¦ Work Order(s) Generated
85 | Veg | KERNERSVILLE skh9815 | GUTHRIE BANK - 03131203 | 6/18/2019 02:00 | 6/18/2019 04:12 | 11252919 | S-CKT - ABC Size: Class 2 FID: 38349981 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | DX Other defect | 29 Conductor, bare | PP Yellow Poplar (tulip) | 23 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,551 | 1552 | 132 | 4031 Reidsville Road | CIRCUIT LOCKOUT. TREE FELL ON PRIMARY BREAKING IT OFF INSULATOR NEAR CHURCHLAND DR & REIDSVILLE RD | Top of poplar tree broken off and fell on 3 phase line @ 4031 Reidsville Rd during thunderstorm in area/tree had vines growing on it/base of tree was 22' from pole line/tree broke neutral in 1 span and knocked middle phase off pole top/crew removed tree and put wire back up/no fu reqr skh9815poss fault locations provided @ 0215. attempted to close breaker @ 0242. offered tech to look into backfeeding at 0245 but was declined due to expected timeframe ~~~ 6/19/2019 ¦ skh9815 ¦ Investigative Action
86 | Veg | RURAL HALL skh9815 | MONTROYAL RET - 03471212 | 6/20/2019 13:49 | 6/20/2019 15:01 | 11256408 | S-CKT - ABC Size: Class 3 FID: 38373603 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | NA | HK Hickory | 45 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,268 | 1267 | 72 | 5754 Stanleyville Dr | CMPL 2019-06-20 15:03:00 by ASADDLE RMK: LOCKOUT TRIP 50 TARGET BC FMAG 2998 | Hickory tree 45' from center of pole line uprooted and fell on 3 phase line @ 5754 Stanleyville Dr/crew cut part of tree from line/no damage to Duke equipment.......Crew removed limb from 3 phase line @ Stanleyville Dr and Alma Dr/skh ~~~ 6/21/2019 ¦ skh9815 ¦ Investigative Action
87 | Veg | RURAL HALL skh9815 | SHATTALN BK - 03301212 | 6/20/2019 13:52 | 6/20/2019 14:48 | 11256423 | S-CKT - ABC Size: Class 3 FID: 38375167 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | NA | OB Oak, white |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,242 | 1258 | 56 | 2185 INDEPENDENCE Road | RH575 CLEARED LIMB OFF LINE AT 2200 INDEPENDENCE AND OPENED 80T TO ISOLATE BROKE POLE AT 2171 JAMESTOWN DUE TO TREE. | Dead limb from white oak tree fell on line @ 2185 Independence Road during thunderstorm /crew removed and put OCB back on/no damage to Duke equipment/circuit to be trimmed 2019/no fu/skh9815 ~~~ 6/21/2019 ¦ skh9815 ¦ Investigative Action
88 | Veg | RURAL HALL skh9815 | N WINSTON - 03231208 | 6/20/2019 13:56 | 6/20/2019 16:07 | 11256460 | S-RCL - ABC Size: 800 VPST FID: 38996795 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | DN No apparent defect | C1 Crossarm, Creosote | PW Pine, white | 50 | F2 Forced Outage | 04 Wind, Rain and Lightning | 585 | 2433 | 131 | 7905 North Point Blvd | CMPL 2019-06-20 16:09:00 by ADBICKF RMK: LOCKOUT...ABC TARGETS...2344 FMAG behind ferguson bath kitchen lighting cabintry building near crick. tree limb on line. | Part of white pine broken off and fell on 3 phase line behind 7905 N Point Blvd during thunderstorm/base of tree was 50' from center line/cracked 8' wood xarm on DDE pole with 3 phase tap/crew removed limb and put recloser back on/FU WO 33165311 to change out arms to fiberglass/skh ~~~ 6/21/2019 ¦ skh9815 ¦ Work Order(s) Generated
89 | Veg - MED | Burlington jhp2990 | FRIEDEN RET - 11172407 | 6/20/2019 14:57 | 6/20/2019 18:58 | 11257013 | S-CKT - ABC Size: Class 2 FID: 38358477 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | NA | HK Hickory | 29 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,436 | 1434 | 241 | BEHIND 901 APPLE STREET | DAMAGE AT 901 APPLE STREET, removed tree and closed breaker, | JHP2990:Hickory tree on back lot line, had to get tree crew with big foot. Cut tree off the double circuit line, closed circuit. Switching was not done with St Marks 2408 open point viper ID 362896923. ~~~ 6/21/2019 ¦ jhp2990 ¦ Investigative Action
90 | Veg - MED | Burlington jhp2990 | FRIEDEN RET - 11172408 | 6/20/2019 14:57 | 6/20/2019 18:58 | 11256997 | S-CKT - ABC Size: Class 2 FID: 38358585 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | NA | HK Hickory | 29 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2,099 | 2100 | 241 | 901 apple st. | CMPL 2019-06-20 19:15:00 by TJMILLI RMK: POSSIBLE LOCKOUT...TREE ON LINE AT 901 APPLE ST GIBSONVILLE..DOUBLE CIRCUIT RUNS IN BACK YARD, large hickory tree fell across both circuits. tree crew contacted. Tree removed, circuits re-energized manually @ stat | JHP2990:Hickory tree on back lot line, had to get tree crew with big foot. Cut tree off the double circuit line, closed circuit. Switching was not done with St Marks 2402 solid blades 39070119. ~~~ 6/21/2019 ¦ jhp2990 ¦ Investigative Action
91 | Veg | HIGH POINT FAPlumm | RANDLMN RD R - 10121206 | 6/20/2019 14:59 | 6/20/2019 16:46 | 11257067 | S-CKT - ABC Size: Class 2 FID: 38354973 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | TF Tree fails, defective | DC Internal stem decay | C1 Crossarm, Creosote | SY Sycamore | 35 | F2 Forced Outage | 04 Wind, Rain and Lightning | 779 | 779 | 107 | 104 Randolph St., Randleman | CMPL 2019-06-20 16:53:00 by MWOOTEN RMK: WOOTEN/EATON CALLED IN. CKT LOCKOUT BC TARGETS 2593 / POSS FAULT LOCATION NEAR HIGH POINT ST AND RANDOLPH ST TO W NAOMI ST AND RAILROAD AV | faplumm..A Sycamore tree 35' from C/L of conductor with internal stem decay fell during a wind and rain event and laid on the conductor. The crew was able to remove the tree and reenergize the circuit. On the investigation a cross arm two spans downstream was broke and the conductor was laying on the guy stick. I called C&M and they sent crew to replace x-arm.. There is a danger tree that is marked at location of the outage, will check with vegetation mgmt. on time frame to remove tree. Pics on server. ~~~ 6/21/2019 ¦ FAPlumm ¦ Investigative Action
92 | Veg | RURAL HALL sba8312 | DANBURY RET - 03382403 | 6/20/2019 15:00 | 6/20/2019 21:30 | 11257099 | S-CKT - ABC Size: Class 3 FID: 38375381 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | TF Tree fails, defective | DE Erosion/poor enviornment | C1 Crossarm, Creosote | PP Yellow Poplar (tulip) | 65 | F2 Forced Outage | 04 Wind, Rain and Lightning | 762 | 764 | 390 | BEHIND 1368 NC 8 AND 89HWY S | EMERGENCY DROP...WIRE DOWN AT METER 319-574-180 BEHIND HOUSE BACK LINE TOWARDS SUNSET PARK....amps still showing on A phase (73) B & C have drop 50 amps FAULT ON NC HWY 8 FROM MOUNTAN RD TO COUNTRY HOME RD | Defective Poplar fell from 65' from line breaking X-arm and 2 spans of 3ph 1/0 Hardwall back property line with no access due to strong storm passing thru while saturating the ground ~~~ 6/24/2019 ¦ sba8312 ¦ Investigative Action
93 | Veg - MED | Chapel Hill omshistproc | EASTGATE RET - 19021204 | 6/20/2019 15:36 | 6/20/2019 18:39 | 11257425 | S-CKT - ABC Size: Class 1 FID: 38358873 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | 03 Tree (Vegetation) | 27 Other/See Notes | 29 Conductor, bare |  |  | F2 Forced Outage |  | 1,824 | 1965 | 183 | plant rd and e franklin st | CMPL 2019-06-20 18:44:00 by BJACOBY RMK: TREE/POLE/LINES DOWN 101 PLANT RD LOCKOUT BG FAULT FMAG 2543 | tree on plant rd broke pole and cause tap wires to break. the unfused three phase on plant rd is what took the circuit out... NO OUTAGE REVIEW INFO
94 | Veg - MED | Chapel Hill omshistproc | GREY - 19091207 | 6/20/2019 15:52 | 6/20/2019 17:14 | 11257577 | S-RCL - ABC Size: 800 VPST FID: 39005248 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 16 Closed Recl or Sectionalizer |  |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 819 | 1883 | 82 | WHIPPORWHILL AND FARRIGNTON | BC LOCKOUT FMAG 1921 / TL524 TEER REMOVED TREE AT WHIPPORWHILL AND FARRINGTON | ... NO OUTAGE REVIEW INFO
95 | Dist | Burlington jhp2990 | GLN RVN MN R - 11042405 | 3/19/2019 14:33 | 3/19/2019 14:58 | 11153534 | S-RCL - ABC Size: 800 VPST FID: 38999230 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | DE Prior damage | 39 Repaired Overhead Conductor | 30 Conductor, covered |  |  | P4 Crew Initiated Outage | 00 Calm | 808 | 1426 | 25 | JHP2990: FRONT & DAVIS STREETS | BILL STIL 434 251 0431 (1 HR) - ATTEMPTED TO CALL BURLINGTON SCHOOL, LINE BUSY - WIRE WAS BURNING | JHP2990: CONTRACTOR CREW WORKING ON CHANGING OUT POLE AT W FRONT STREET & DAVIS STREET.CREW SETTING UP AND PUTTING COVER ON LINE AND NOTICE A WIRE WITH ONLY 3 STRANDS HOLDING. CREW CALLED IN WITH WHAT THEY FOUND, AND THAT THEY NEEDED TO DISSCONNECT THE POWER AT THE RECLOSER. THE RECLOSER WAS DROPPED AND THE WIRE REPAIRED. ~~~ 3/20/2019 ¦ jhp2990 ¦ Investigative Action
96 | Dist | Greensboro ELamb | PLEASNT GARD - 09791203 | 3/20/2019 14:09 | 3/20/2019 14:53 | 11154313 | S-CKT - ABC Size: Class 1A FID: 38357433 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | HR Reclose Block, fault occurred | 14 Closed Breaker | 29 Conductor, bare | M3 R Milbank |  | F2 Forced Outage | 00 Calm | 967 | 966 | 44 | 6305 Hunt Rd | B G FAULT FMAG 3988 caj3396 tree fell onto primary while under HLT | ELamb: Behind 6305 Hunt Rd, crew had the circuit on one shot for planned work. Due to slack conductors the middle phase, which is the B phase sagged into the neutral and caused the circuit to lockout. The crew used one auto splice to resagged the middle phase primary and 2 auto splices for the neutral. The investigation required several ride outs to this location due to the complexity determining the cause of the outage. ~~~ 3/28/2019 ¦ ELamb ¦ Investigative Action
97 | Dist | MT AIRY sba8312 | LEVEL CROSS - 28041201 | 3/21/2019 13:35 | 3/21/2019 13:43 | 11154996 | RCL3 - ABC Size: 560 WVE FID: 39004937 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | D1 Broken/Malfunctioning | 16 Closed Recl or Sectionalizer | 44 Regulator |  |  | P4 Crew Initiated Outage | 00 Calm | 772 | 961 | 8 | bad regulator fac id 39012810 | Josh Wiles to have open 980 239 8549 to repair bad regulator fac id 39012810 | Crew had Bad Regulators at 39012810, need to open RCL to bypass Regulators. DCC was not able to communicate crew had to bypass ELEC RCL due to control cable prongs melted in the plug. Crew C/O Interupter on WO 32027076, Modified time according to PI Data ~~~ 3/28/2019 ¦ sba8312 ¦ Work Order(s) Generated
98 | Dist | Greensboro ELamb | KILDARE - 09082410 | 3/23/2019 19:05 | 3/23/2019 23:31 | 11156379 | S-RCL - ABC Size: 800 VPTT FID: 38998999 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | PP Pole |  |  | F2 Forced Outage | 00 Calm | 827 | 3209 | 266 | 1048 Summitt Ave | OFF TO REPLACE BROKE POLE...REPLACE 40/5 POLE FROM WRECK | ELamb: Due to a car accident, crew had to initiated outage to replace broken 40/5 pole at 1048 Sumitt Ave. No follow up were needed ~~~ 3/25/2019 ¦ ELamb ¦ Investigative Action
99 | Dist | KERNERSVILLE lmh9203 | BROAD ST RET - 03411202 | 3/24/2019 16:40 | 3/24/2019 17:32 | 11156624 | S-CKT - ABC Size: Class 3 FID: 38350461 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 17 Tree error, public | 37 Removed Limb or Tree From Lin | NA | PP Yellow Poplar (tulip) |  | F2 Forced Outage | 00 Calm | 932 | 974 | 52 | 2335 KONNOAK VIEW | CMPL 2019-03-24 18:00:00 by CTRIPP RMK: SCKT OUTAGE TARGET AB FMAG 3543 TRIP 51...HALO OFF W ACADIA AVE & KONNOAK DR, TREE ON LINE ON FIRE, EVENT 11156627 | AT 2335 KONNOAK VIEW DR, A CUSTOMER WAS CUTTING TREE LIMBS OUT OF A POPLAR TREE AND ONE FELL ON TO THE 3P PRIMARY TRIPPING THE CKT OFF. CRETATED WO# 33180199 TO REPAIR BROKEN CONDUCTOR....lmh ~~~ 3/25/2019 ¦ lmh9203 ¦ Work Order(s) Generated
100 | Dist | Reidsville gla4211 | GATEWOOD - 17131203 | 3/26/2019 08:36 | 3/26/2019 08:42 | 11157539 | S-RCL - ABC Size: 560 WVE FID: 39007379 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | 20 Equipment failure | 47 Replaced Pole | PX Insulator, polymer |  |  | F2 Forced Outage | 00 Calm | 594 | 1338 | 6 | Shady Grove Rd and Rock Quarry Rd | RE72 REQ TO OPEN RCL LONG ENOUGH TO CUT JUMPERS TO CLEAR UP WIRE DOWN AT SHADY GROVE RD ROCK QUARY RD. UNABLE TO OPEN SWITCH OR FUSE. WOULD REQ FLAGGERS AND WIRE WAS ON GROUND BURNING. | G Akers .. Pole top burned in two at top bolt on transformer bracket and pole top fell over. This was the deadend pole at intersection of Shady Grove Rd and Rock Quarry Rd. Dead end bolt also pulled out of pole when pole burned and middle phase fell to ground. Most likely deadend failed and caused pole fire. Deadend was a polymer deadend. Pole and equipment was disposed of at time of investigation. The 65T middle phase fuse on Old US 29 north of Goodman Rd blew. When linemen arrived on site wire was sparking because the two outside phase were still hot. They asked for the electronic recloser to be opened to cut jumpers to de-energize conductors to burned pole. See event # 11157671 for 65T fuse outage and event # 11157602 for jumper outage. ~~~ 4/2/2019 ¦ gla4211 ¦ Investigative Action
101 | Dist | LEWISVILLE lmh9203 | LEWISVILLE - 03201206 | 3/30/2019 22:07 | 3/31/2019 00:32 | 11160757 | S-CKT - ABC Size: Class 3 FID: 38350089 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M7 Penta | P2 Pole, CCA | CX CPI | 11 | F2 Forced Outage | 00 Calm | 1,529 | 1529 | 145 | 605 LEWISVILLE VIENNA RD | LOCK OUT...VEHICLE ACCIDENT & BROKEN POLE NEAR 605 LEWISVILLE VIENNA RD. WAGNER & JEFF WERE ABLE TO FLOAT WIRE, REMOVED TREE FROM MID SPAN AND CLOSED BREAKER. REPAIRS TO BE SCHEDULED DURING NORMAL WORK HOURS. | A VEHICLE RAN OFF THE ROAD IN A CURVE, AT 605 LEWISVILLE-VIENNA RD, THE VEH HIT A 40/5 POLE AND BROKE IT ABOVE GROUND LEVEL. CONDUCTORS SLAPPED TOGETHER AND TRIPPED THE CIRCUIT OFF. THE OWS SEC WERE WRAPPED UP IN A TREE. CREWS SECURED THE POLE AND MADE SAFE. CIRCUIT WAS RE-ENERGIZED...CREATED WO# 32354554 TO INSTALL SWITCHES TO ISOLATE FUTURE OUTAGES CAUSED BY VEHICLE ACCIDENTS IN THIS AREA....lmh ~~~ 4/2/2019 ¦ lmh9203 ¦ Work Order(s) Generated
102 | Dist | HIGH POINT FAPlumm | FAIR GROVE RET - 10251204 | 3/31/2019 09:16 | 3/31/2019 10:24 | 11160875 | S-CKT - ABC Size: Class 3 FID: 38374860 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | MS Steel | G1 Guywire |  |  | F2 Forced Outage | 00 Calm | 1,343 | 1344 | 68 | Prior to 791 Tower Road, in curve | CMPL 2019-03-31 10:49:00 by DMBROW2 RMK: LOCKOUT - TRIP INST - TARGETS A B C - fmag 3021 - possible fault off Don Truell Ln near DG rcl --- 2nd location Tower Rd between S Old Raleigh Rd and Quail Ln - just downstream of 200L recloser | faplumm..A vehicle ran off of the road at the sharp curve on Tower Road clipping a guy wire and causing the wire to wrap around all three phases of primary conductor. Crew was able to remove guy wire and reenergize the circuit. The accident was located downstream of a set of hydraulic reclosers but due to the FC the station locked out prior to the reclosers. All Duke equipment appeared to operate correctly. PIC's on the R&I server. I have created work order 32208188 to have a new guy wire and anchor installed at this location. ~~~ 4/4/2019 ¦ FAPlumm ¦ Work Order(s) Generated
103 | Dist | ELKIN sba8312 | YADKINVILLE - 29061205 | 4/10/2019 14:49 | 4/10/2019 15:38 | 11168666 | S-CKT - ABC Size: Class 1 FID: 38348819 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 00 Calm | 1,284 | 1290 | 49 | NO FAULT FOUND | Ckt lockout. AG TARGETS. 1257 FMAG Billy Bowman has ckt blocked, all his crews OK. They did not cause. Kent Suddreth/Supv aware. POSSIBLE FAULT LOCATION DOWN OLD 421 FROM TRACEY TO RCL AT CENTER....RODE OUT CIRCUIT AND NOT FAULT FOUND | Crew had circuit blocked while they were working on reconductoring project, looked at a area where the fault current plotted did not find anything weather was calm no other events happened at that time that would have contributed to the circuit locking out. ~~~ 4/15/2019 ¦ sba8312 ¦ Investigative Action
104 | Dist | Burlington jhp2990 | GLN RVN MN R - 11042410 | 4/11/2019 09:32 | 4/11/2019 10:38 | 11169391 | RCL - ABC Size: 200 4E FID: 38999247 | 02 Line Recloser | OH Distribution Line Overhead | 05 Planned (IEEE) | D2 Decayed | 54 Scheduled | CR Crossarm |  |  | P7 Customers Notified | 00 Calm | 555 | 2122 | 66 | Flora Ave & Durham St Est. | ROBERT GAULT 336-520-5609 OPENED RECLOSER TO CUT JUMPERS TO ISOLATE BROKEN CROSSARM - PLANNED OUTAGE - JUMPERS MODELED IN DOMS AND DMS - WILL CALL BACK WHEN RECLOSER CLOSED IN | jhp2990: RECLOSER DROP TO CUT JUMPERS ON JUCTION POLE TO REPLACE ROTTEN CROSSARMS ON OUTAGE EVENT 11169473 72 CUSTOMERS. ~~~ 4/15/2019 ¦ jhp2990 ¦ Investigative Action
105 | Dist | Madison gla4211 | MADISON - 51061203 | 4/11/2019 12:19 | 4/11/2019 13:22 | 11169582 | S-RCL - ABC Size: 560 WVE FID: 39005224 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | HR Reclose Block, fault occurred | 16 Closed Recl or Sectionalizer |  |  |  | F2 Forced Outage | 00 Calm | 1,765 | 1816 | 63 | 548 SHELTON RD STOKESDALE | LOCK OUT...TARGETS BG & FMAG 678..JAMES BULLINS CREWS RIDING OUT-CHECK WITH MICHAEL HITCHINSON/ECC 336-430-2819 BEFORE ENERGIZING. SAILBOATS MAST MADE CONTACT WITH LINES AS IT WAS BEING PULLED OUT OF STORAGE @ 548 SHELTON RD STOKESDALE. | G Akers .. this electronic recloser was blocked for construction work being done at the circuit exits for the new Ellisboro substation. A sailboat was being pulled to the boat ramp at Belews Lake and was pulled straight to the road and the mast made contact with the three phase line on the road. This recloser would not have opened if it had not been blocked. The recloser on Shelton Rd would have cleared the fault. The conductor was damaged and WO # 32473325 was created to make repairs on the conductor. ~~~ 4/15/2019 ¦ gla4211 ¦ Work Order(s) Generated
106 | Dist | Burlington jhp2990 | GLN RVN MN R - 11042410 | 4/11/2019 12:53 | 4/11/2019 15:11 | 11169620 | RCL - ABC Size: 200 4E FID: 38999247 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D2 Decayed | 16 Closed Recl or Sectionalizer | C2 Crossarm, Penta |  |  | P4 Crew Initiated Outage | 00 Calm | 555 | 2122 | 138 | Flora Ave & Durham St Ext | ROBERT GAULT 336-520-5609 OPENED RECLOSER TO make JUMPERS up LIGHTS FLICKERING | JHP2990:FIRST OUTAGE 11169391, RECLOSER OPEN UP A SECOND TIME TO MAKEUP JUMPERS SAFELY. THE PLAN WAS TO MAKE THE JUMPER BACK WITH NO LOAD ON THEM ONLY PICKING UP THE WIRE, BUT THE CREW SAID IT WAS NOT SAFE. ~~~ 4/24/2019 ¦ jhp2990 ¦ Investigative Action
107 | Dist | Greensboro ELamb | KILDARE - 09082412 | 4/12/2019 15:30 | 4/12/2019 17:11 | 11170558 | S-RCL - ABC Size: 800 NVST FID: 39009333 | 02 Line Recloser | OH Distribution Line Overhead | 19 Lightning strike | HZ Cause undetermined | 16 Closed Recl or Sectionalizer | 29 Conductor, bare |  |  | F2 Forced Outage | 02 Rain | 1,005 | 1909 | 101 | N/A | CMPL 2019-04-12 17:14:00 by JDM7341 RMK: RCL locked out- Rec a hndl down alarm-SHT disabled. | ELamb: We had a severe lightning storm that had affect this area. When checking roads it showed the recloser amps drop but did not show a fault when looking under fault analysis in Roads. After this I proceeded to check ESNET and found out I could not access this recloser in esnet, so I had to drove out to the device to get the data off the control panel. When checking the SEL data on the control panel of recloser it did not show the operation because the data log was full showing the last operation was record during the ice storm earlier this year. Cyme study could not be ran because their was no fault magnitude recorded. Work order 32410228 was created to check to see if recloser is still working properly. Equipment inspectors checked the recloser and everything was found to be operating correctly. Rode from Recloser to end of line and any associated outages and did not identify anything that would've caused this Recloser to lock out. ~~~ 4/18/2019 ¦ ELamb ¦ Work Order(s) Generated
108 | Dist | LEWISVILLE lmh9203 | PFAFFTOWN RET - 03271201 | 4/13/2019 20:48 | 4/13/2019 21:31 | 11171535 | S-CKT - ABC Size: Class 3 FID: 38376257 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | MP Porcelain | 38 Insulator | IC ICB | 4 | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 1,328 | 1341 | 43 | 2569 OLIVET CHURCH RD | OPENED BRKR FOR CRWS TO C/O SOH:381646568..ONLY TWO WORKERS..COULD NOT USE ANY BACKFEED OPTIONS DUE TO AVAILIBLE WORKERS AND BRKR SHOULD ONLY BE OFF FOR 45 MIN....opened circuit due to burned up switches...SOH:381646568 on fire had to c/o | AT 2569 OLIVET CHURCH RD, THE C-PH 600A VERTICAL SWITCH CAUGHT FIRE UNDER A SET OF 2004 ICB DEAD END INSULATORS. CAUSED BY LIGHTNING OR A BAD DE INSULATOR. ALOT OF LIGHTNING IN THE AREA. CREATED WO# 32320011 TO C/O ARM TO 10', DE's AND SWITCHES.....lmh ~~~ 4/15/2019 ¦ lmh9203 ¦ Work Order(s) Generated
109 | Dist | Greensboro gla4211 | LAKE TOWNSEND RET - 09302401 | 4/14/2019 18:08 | 4/14/2019 18:33 | 11173733 | S-CKT - ABC Size: Class 3 FID: 384600729 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | 22 Inadequate Clearances | 14 Closed Breaker |  |  |  | F2 Forced Outage | 17 Wind and Rain | 1,320 | 1327 | 25 | N Church St and Spencer-Dixon Rd | CIRCUIT DROPPED TO REPAIR WIRE APPROX 30 MIN - PRIMARY BURNING | G Akers .. phase conductor and span guy are getting together midspan when sag on wire changes. WO # 32522154 was created to extend double circuit one more span to next pole so that span guys could be removed. ~~~ 4/15/2019 ¦ gla4211 ¦ Work Order(s) Generated
110 | Dist | RURAL HALL skh9815 | N WINSTON - 03231203 | 4/15/2019 17:49 | 4/15/2019 21:03 | 11176820 | RCL - ABC Size: 200 V4L FID: 38996686 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA |  |  | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 723 | 1962 | 194 | 4619 Ogburn Avenue | CMPL 2019-04-15 21:45:00 by PWP7277 RMK: CMPL 2019-04-15 21:40:00 by ETCHILD RMK: OPENED 200VAL RCL ETA 2HRS VENICLE ACCIDENT POLE AND LINES DOWN ETA 15-20 @ 1755 | Vehicle accident @ 4619 Ogburn Avenue 1 span past reclosers/40/5 straight line pole with 25 kva broken at neutral level/crew dropped reclosers to change out pole/no fu reqr skh9815 ~~~ 4/16/2019 ¦ skh9815 ¦ Investigative Action
111 | Dist - MED | RURAL HALL skh9815 | MT TABOR BNK - 03221206 | 4/19/2019 14:38 | 4/19/2019 17:51 | 11180897 | S-CKT - ABC Size: Class 3 FID: 38349969 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | D4 Burned/Exploded | MA Aluminum | 73 Compression |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,641 | 1642 | 193 | CORAVAN ST & JEFFERSON FOREST CT | CMPL 2019-04-19 17:54:00 by JTC0364 RMK: CKT LOCK OUT FMAG AB 2265 - POSSIBLE FAULT ON SHATTALON BETWEEN PHIL PARK AND SUNNYDELL ALONG DOUBLE CIRCUIT | CREW FOUND 4/0 CU JUMPER BURNED @ CONNECTOR ON BOTTOM PHASE ON VERTICAL POLE ON CORAVAN ST & JEFFERSON FOREST CT/CREW REPLACED JUMPER WITH 2 1/0 CU AND REPLACED CONNECTOR/FU WO 32451848 TO REPLACE JUMPER WITH 4/0 CU AND CHECK CONNECTORS ON OTHER PHASES/SKH9815 ~~~ 4/22/2019 ¦ skh9815 ¦ Work Order(s) Generated
112 | Dist | Reidsville jhp2990 | MONROETON - 17121202 | 4/22/2019 00:09 | 4/22/2019 05:11 | 11184979 | S-CKT - ABC Size: Class 3 FID: 38371141 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 14 Closed Breaker | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 595 | 598 | 302 | flatrock rd & hwy 158 intersectio | CMPL 2019-04-22 05:14:00 by JMW2989 RMK: CIRCUIT LOCKOUT... HIT POLE vehicle struck guys causing them to wrap around dbl cir. . burnind down 2- phases, | JHP2990: WORK ORDER CREATED TO REPAIR THE CROSS ARM BRACE AND THE GUY WIRE. CREW DIDN'T CHANGE THE CROSS ARM BRACE OR PULL ONE OF THE TWO PRIMARY GUY AND NEUTRAL GUY WO 32402631 TO FIX THE PROBLEM ~~~ 4/23/2019 ¦ jhp2990 ¦ Work Order(s) Generated
113 | Dist | Chapel Hill rlw2159 | EASTGATE RET - 19021206 | 4/22/2019 15:23 | 4/22/2019 22:28 | 11185712 | SOH - ABC Size: 600 Line Disconnect FID: 84420415 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P1 Pole, Creosote |  |  | F2 Forced Outage | 00 Calm | 730 | 1097 | 425 | 500 WEAVER DAIRY RD | CMPL 2019-04-22 23:00:00 by CRBARWI RMK: OPENED SOLIDS 84420415 TO ENERGIZE CIRCUIT AND ISOLATE POLE AT PL: 363384412 - FAULTED RIGHT BEFORE LINE RECLOSER 39005400 | rlw2159-car broke pole, solid blades opened at FID# 84420415 to get circuit back on. ASSOCIATED tickets 11185597(blink), 11185600(circuit) and 11186136(open ckt to close solid blades ~~~ 4/24/2019 ¦ rlw2159 ¦ Investigative Action
114 | Dist | HIGH POINT FAPlumm | HOLLY HILL R - 10161206 | 4/24/2019 20:03 | 4/24/2019 22:27 | 11189074 | S-CKT - ABC Size: Class 3 FID: 38354961 | 01 Feeder Breaker/Recl in Substa | UG Distribution Line Underground | 20 Equipment failure | D4 Burned/Exploded | M3 Copper | EF Termination HV 600 amp |  |  | F2 Forced Outage | 00 Calm | 1,612 | 1615 | 144 | Holly Hill 12-06 terminations @ breaker | CMPL 2019-04-24 22:48:00 by JSGALLI RMK: LOCKOUT FMAG 7124...CUST REPORTS POSS FIRE AT SUBSTATION...TERMINATIONS ON BUS COMING OUT OF SUBSTATION FOR 1206 BURNT...SWITCHING LOAD FROM 1206 TO 1209 | faplumm..The termination on the ug cable malfunctioned causing a circuit outage. Crews were able to swap the customers on the 12-06 circuit over to the 12-09 circuit, which is the auxiliary circuit. Crews will replace the termination during the week of April 29th on work order 32448581 . PIC's on R&I server. ~~~ 4/25/2019 ¦ FAPlumm ¦ Work Order(s) Generated
115 | Dist - MED | HIGH POINT FAPlumm | HOLLY HILL R - 10161206 | 4/26/2019 18:03 | 4/26/2019 19:15 | 11195016 | S-RCL - ABC Size: 800 VPST FID: 38998435 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | D1 Broken/Malfunctioning | 16 Closed Recl or Sectionalizer | 43 Recloser, Electronic |  |  | F2 Forced Outage | 17 Wind and Rain | 1,174 | 1615 | 72 | E. Meadow Road and Pine Heights Cir. | LOCKOUT TARGET ABCG FMAG UNKNOWN. broke pole at corner 45/3 | faplumm...A single phase pole behind two sets of switches broke during a high wind event causing the electronic recloser to lock out. Upon further investigation this electronic recloser has a battery alarm which causes the recloser to be automatically put on one shot. The crews rode the electronic backbone and found no reason for the lockout. According to ProComm date the recloser only had one trip on 4/26/2019. I have spoken with the equipment inspectors and they are aware of this location and are working with different groups to investigate this issue. SEL group was able to dial into the recloser and make some updates and the battery alarm has been cleared. ~~~ 4/29/2019 ¦ FAPlumm ¦ Investigative Action
116 | Dist | Greensboro ELamb | LINDELL ROAD - 09480403 | 4/27/2019 07:02 | 4/27/2019 11:16 | 11196890 | S-RCL - ABC Size: 560 WVE FID: 39005708 | 02 Line Recloser | OH Distribution Line Overhead | 05 Planned (IEEE) | 07 Proactive Work | 14 Closed Breaker | 48 Transformer |  |  | P2 Scheduled Outage | 00 Calm | 617 | 608 | 254 | 200 N Lindell Rd | PLANNED OUTAGE ON TRANSMISSION SIDE | ELamb: At 200 N Lindell Rd, Transmission had a schedule outage to change the transformer out in the substation that feed the Lindell Circuits. Lindell Rd Dist 09480403 circuit breaker is the 560 WVE recloser facility id 39005708. ~~~ 5/3/2019 ¦ ELamb ¦ Completion Codes or Remarks
117 | Dist | HIGH POINT FAPlumm | HOLLY HILL R - 10161206 | 4/27/2019 08:34 | 4/27/2019 08:53 | 11196990 | S-RCL - ABC Size: 800 VPST FID: 38998435 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | D1 Broken/Malfunctioning | 16 Closed Recl or Sectionalizer | 43 Recloser, Electronic |  |  | F2 Forced Outage | 17 Wind and Rain | 1,174 | 1615 | 19 | E Meadow Road and Pine Heights Cir. | RECLOSER LOCKOUT//FAULT HALOS SHOWED WHERE POLE BEING REPAIRED E MEADOW AND PINE HEIGHTS/FMAG 64 A C/POLE DOWN FROM E MEADOW AND PINE HEIGHTS MOVED JUST ENOUGH TO BRING METAL EXTENSION INTO CONTACT WITH WIRES,LOCKING OUT RCL | faplumm...A single phase pole behind two sets of switches broke during a high wind event causing the electronic recloser to lock out. Upon further investigation this electronic recloser has a battery alarm which causes the recloser to be automatically put on one shot. The crews rode the electronic backbone and found no reason for the lockout. The crews were changing out the pole on 4/27/2019 and the metal arm came in contact with the primary conductor which automatically locked out the electronic recloser. According to ProComm date the recloser only had one trip on 4/26/2019. I have spoken with the equipment inspectors and they are aware of this location and are working with different groups to investigate this issue. SEL group was able to dial into the recloser and make some updates and the battery alarm has been cleared. ~~~ 4/29/2019 ¦ FAPlumm ¦ Investigative Action
118 | Dist | Burlington jhp2990 | PLSNT GRV RT - 11181203 | 4/27/2019 16:41 | 4/28/2019 05:08 | 11198179 | S-CKT - ABC Size: Class 3 FID: 38359185 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA |  |  | F2 Forced Outage | 03 Wind | 829 Cust Eq: 456 | 1285 | 747 | JHP2990: 4375 NC 49 | CKT LOCKED OUT DUE TO BROKE DOUBLE CKT POLE / ORIGINAL EVENT CLOSED IN ERROR DURING INTEGRITY CHECK | JHP2990: DOUBLE CIRCUIT POLE HIT BY VEHICLE DROPPED CIRCUIT FOR POLE / BACK ENG ENTRAPMENT..NEED 45 CLASS 3 POLE, 2-10FT REG WOOD XARM,2-8FT REG WOOD XARMS, 12-10'S IN INSULATORS, 2-PRIMARY AND NEUTRAL DEAD ENDS ENTRAPMENT/HIT. LOAD WAS TRANSFERRED TO HAW RIVER 1203 BY VIPER OPENED ID 39004573 AND CLOSING THE OPEN POINT VIPER ID 406508998. ~~~ 5/1/2019 ¦ jhp2990 ¦ Investigative Action
119 | Dist | Burlington jhp2990 | PLSNT GRV RT - 11181204 | 4/27/2019 16:41 | 4/28/2019 05:08 | 11197884 | S-CKT - ABC Size: Class 3 FID: 38372604 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA |  |  | F2 Forced Outage | 03 Wind | 719 | 721 | 747 | JHP2990:4375 NC 49 NORTH | DROPPED CIRCUIT FOR ENTRAPMENT/HIT POLE EVENT 11197846 / NO BACK FEED OPTIONS FOR CKT 1204 PER GRID ENG ENTRAPMENT..NEED 45 CLASS 3 POLE, 2-10FT REG WOOD XARM,2-8FT REG WOOD XARMS, 12-10'S IN INSULATORS, 2-PRIMARY AND NEUTRAL DEAD ENDS | jhp2990: SAME OUTAGE AS PLEASANT GROVE 1203 EVENT 11198179. DROPPED CIRCUIT /HIT POLE / NO BACK FEED OPTIONS FOR CKT 1204 PER GRID ENG ENTRAPMENT..NEED 45 CLASS 3 POLE, 2-10FT REG WOOD XARM,2-8FT REG WOOD XARMS, 12-10'S IN INSULATORS, 2-PRIMARY AND NEUTRAL DEAD ENDS ~~~ 5/1/2019 ¦ jhp2990 ¦ Investigative Action
120 | Dist | Burlington jhp2990 | PLSNT GRV RT - 11181203 | 4/28/2019 10:16 | 4/28/2019 10:32 | 11198292 | S-RCL - ABC Size: 800 VPTT FID: 406508998 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | 16 Accident, public vehicle | 47 Replaced Pole | P1 Pole, Creosote |  |  | F2 Forced Outage | 00 Calm | 1,285 Cust Eq: 1285 | 1285 | 16 | JHP2990:1126 NC-49 |  | JHP2990:POLE HIT, BROKEN, AT ONE SPAN NORTH OF VIPER ID 405559762.VIPER STILL HOT WHEN CREW ARRIVED.DROPPED VIPER ID 405559762 FOR ENTIRE OUTAGE 111 CUSTS AND CUT JUMPER AT BEARBERRY TRAIL TX ID 39547997 111 . OPEN POINT VIPER ID 406508998 CLOSED AFTER JUMPERS CUT RESTORING 1285 CUSTOMERS. ~~~ 5/10/2019 ¦ jhp2990 ¦ Investigative Action
121 | Dist | KERNERSVILLE skh9815 | OAK RIDGE - 03241207 | 5/5/2019 07:35 | 5/5/2019 10:32 | 112055611 | SolidBar - ABC Size: 300 Solid Bar FID: 454305571 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA |  |  | F2 Forced Outage | 00 Calm | 961 | 1006 | 177 | 410 N Main Street | KV570 PULLED SOLIDS/BROKE POLE | Vehicle accident @ 410 N Main Street/45/3 straight line double circuit pole with 150 kva bank broken at base/crew cut jumpers @ Main St & Adams St & closed switches @ 454305571 to swap load to Kernersville 1203/see event112055613 for disconnect outage & 11205544 for Oak Ridge 1208 outage/crew changed out pole and 150kva bank/load swapped back to normal on 05/08/19/no fu reqr skh9815 ~~~ 5/7/2019 ¦ skh9815 ¦ Investigative Action
122 | Dist | Burlington jhp2990 | WHITSETT - 11202409 | 5/6/2019 12:13 | 5/6/2019 15:09 | 11206810 | S-RCL - ABC Size: 800 VPST FID: 363861313 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | HR Reclose Block, fault occurred | 16 Closed Recl or Sectionalizer | UG Cable, UG, 25KV 1/0 |  |  | F2 Forced Outage | 00 Calm | 1,562 | 3920 | 176 | CLEARWATER WAY & GAIRLOCH TRCE | LOCK OUT...TARGET AG FMAG 1778 - LOCK OUT WHILE UNDER HLT. BOBBY SUTTON CHECKING..POSSIBLE CUT UG NEAR 152/119 GAIRLOCH TERRACE | JHP2990: OH CREW HAD HLT ON THIS RECLOSER ID 363861313 WHILE THEY WERE WORKING OUT A POLE AT HWY 70 AND NC HWY ID6187246014 . AT&T CONTRACTOR WHILE DIGGING POT HOLE BY HAND AT GAIRLOCH TRACE ID 465865036, DIGING AROUND THE PRIMARY THE SHOVEL HIT A ROCK AND BOUNCED OFF THE ROCK AND HIT THE PRIMARY EVENT 11207065.THE 65E FUSE DIDN'T BLOW ID 38914275, THIS HLT ON THE RECLOSER TOOK THE RECLOSER OUTON EVENT 11206810. ~~~ 5/7/2019 ¦ jhp2990 ¦ Investigative Action
123 | Dist | MT AIRY sba8312 | BANNERTOWN - 28061207 | 5/7/2019 07:01 | 5/7/2019 07:19 | 11207488 | S-CKT - ABC Size: Class EX FID: 38351373 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | HW Mid Span Fault | 47 Replaced Pole | P1 Pole, Creosote |  |  | F2 Forced Outage | 00 Calm | 858 | 1158 | 18 | 692 OLD US 52 SOUTH | BREAKER LOCK OUT...VEHICLE ACCIDENT 692 OLD US 52 SOUTH. BREAKER AND RECLOSER 120134141 LOCKED OUT. CREW CONFIRMED FAULT ADDRESS DOWNSTREAM OF RECLOSER 120134141 - CLOSED BREAKER. JOSH CHILDRESS | Mid-Span fault near 2778 S. Main St. locked out OCB,Vehicle ran off road hitting Guywire and breaking pole, crew opened ELEC RCL (event 11207496 ) , and got OCB back on. crew replaced pole and guywire, no F.U.N. .... Pics on R&I Server 20190507-11207488-Bannertown 28061207 ~~~ 5/8/2019 ¦ sba8312 ¦ Work Order(s) Generated
124 | Dist | HIGH POINT FAPlumm | HOLLY HILL R - 10161211 | 5/9/2019 10:58 | 5/9/2019 13:13 | 11209607 | RCL - ABC Size: 200 V4L FID: 38998555 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | D1 Broken/Malfunctioning | M8 Creosote | C1 Crossarm, Creosote |  |  | F2 Forced Outage | 00 Calm | 548 | 1199 | 135 | Cannon St. & Fisher Ferry St. | RCL OUTAGE | faplumm...A cross arm at the intersection of Cannon St. and Fisher Ferry St. broke causing a span of #2CU to break. Crew was able to replace the cross arm and repair the overhead conductor. I have created work order 32671893 to have solid door cutouts installed for an isolation point. ~~~ 5/13/2019 ¦ FAPlumm ¦ Work Order(s) Generated
125 | Dist | Burlington jhp2990 | GLN RVN MN R - 11042410 | 5/15/2019 15:59 | 5/15/2019 16:48 | 11215701 | S-CKT - ABC Size: Class 1A FID: 38357649 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | HR Reclose Block, fault occurred | 14 Closed Breaker | F2 Fuse Link |  |  | F2 Forced Outage | 00 Calm | 2,112 | 2122 | 49 | 2234 BURCH BRIDGE RD | CKT LOCKOUT/WAS ON ONE SHOT/CREW STS THEY WERE NOT IN THE AIR/FMAG 1093 A G TRIP INST 50/ ROBERT GAULT RIDING OUT/LARGE TREE ON LINE ST REGIS AND BURGIS BRIDGE PINGING | JHP2990: WHILE PIKE CREW HAD A HLT WHILE THEY WERE WORKING ON THE POLE, THIS TX WITH VINES, CAUGHT ON FIRE AND BLEW THE TX FUSE, WHICH TOOK OUT THE CIRCUIT.AT ID 39536062. WO 2402356 TO CHANGE OUT THE POLE AND INSTALL 10' ~~~ 5/16/2019 ¦ jhp2990 ¦ Work Order(s) Generated
126 | Dist | Greensboro ELamb | RANDOLPH - 09042404 | 5/17/2019 14:43 | 5/17/2019 15:58 | 11217108 | S-CKT - ABC Size: Class EX FID: 38356821 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | PP Pole |  |  | F2 Forced Outage | 00 Calm | 672 | 1055 | 75 | 847 S Elm st | CIRCUIT L/O...POLE HIT 847 S ELM ST - BROKEN 45/3 POLE - NEEDS 8FT WOOD/10FT FIBERGLASS - FLAGGERS REQUESTED BY J RYAN/C DAVIS AT 1530 - POLE WILL BLOCK THE ROAD | ELamb: At 847 S Elm St, a car hit the pole facility id 38536598. The impact of the car caused the pole to break causing the circuit outage for event #11217108. Crew open a set of switches facility id 363663219 for event #11217193 to isolate the fault and restore 672 customer to get the circuit breaker back on, close in recloser facility id 409866618 to restore 217 customer for event #112171931, close in a set of switch facility id 39036839 to restore 140 customer for event 112171932. ~~~ 5/20/2019 ¦ ELamb ¦ Investigative Action
127 | Dist | Burlington jhp2990 | PLSNT GRV RT - 11181203 | 5/19/2019 15:19 | 5/19/2019 18:43 | 11218149 | S-CKT - ABC Size: Class 3 FID: 38359185 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 46 Replaced Insulator | 38 Insulator |  |  | F2 Forced Outage | 00 Calm | 1,280 | 1285 | 204 | JHP2990: ON HWY62 BEFORE HWY 49 | broken bells on pole, less than 90mins to repair. switching wasnt used due to short duration | JHP2990: BROKEN BELLS, CHANGED 6 BELLS,UNABLE TO SWITCH WITH HOPEDALE 1201, WIRE TO SMALL. WO 27344342 & 27337853 CAPICITY FEEDER WORK ORDER TO MAKE TIE. 9.9 MILES. GIP WORK 12/31/1029 ~~~ 5/20/2019 ¦ jhp2990 ¦ Investigative Action
128 | Dist | Greensboro gla4211 | DENNY ROAD - 09252404 | 5/22/2019 12:02 | 5/22/2019 12:36 | 11220856 | RCL - ABC Size: 200 4E FID: 39010244 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P1 Pole, Creosote |  |  | F2 Forced Outage | 00 Calm | 1,170 | 3688 | 34 | 2202 LEES CHAPEL RD | DROPPED RCL DUE TO BROKEN POLE FOR E#11220906 - WILL BE OFF FOR SHORT DURATION | G Akers .. vehicle accident at 2202 Lees Chapel Rd broke pole. New pole was set and all the work that could be done safely energized was completed. Recloser was pulled off to transfer wire that could not be safely done energized. ~~~ 6/5/2019 ¦ gla4211 ¦ Investigative Action
129 | Dist | RURAL HALL skh9815 | MT TABOR BNK - 03221204 | 5/23/2019 06:34 | 5/23/2019 10:39 | 11221446 | S-CKT - ABC Size: Class 3 FID: 38349717 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | HW Mid Span Fault | M1 AAC | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 757 | 2014 | 245 | 120 Norman Road | LOCK OUT...TARGETS AB & FMAG 2882 /---HALO BETWEEN STATION AND NORMAN RD AND SALLY KIRK RD---ALSO DOWN NORMAN RD N TALISON DR. UNKNOWN CAUSE. TECHS RODE OUT LINE AND DID NOT LOCATE FAULT | Overgrown primary on Petree Road in span between Mt Tabor Court & Gatehaven Rd behind 200L's/fault cascaded to backbone/found span faults @ 120 Norman Road/opened blades @ 39027189 to get circuit back on/cut tree limb from primary & restored blades; then opened 300amp doors @ 39076588 & downstream reclosers & 100T's to sectionalize before re-energizing/see events 11221806,11221572,11230811 & 11221807/count modified/issued WO 32806145 for tree work & 32831999 to change out pole & install 10' arms/skh9815 ~~~ 5/24/2019 ¦ skh9815 ¦ Work Order(s) Generated
130 | Dist | RURAL HALL skh9815 | MT TABOR BNK - 03221204 | 5/23/2019 06:34 | 5/23/2019 12:13 | 11221572 | FOH_SolidB - ABC Size: 300A solid FID: 39076588 | 08 Disconnect | OH Distribution Line Overhead | 28 Other Cause | HW Mid Span Fault | M1 AAC | 29 Conductor, bare |  |  | P4 Crew Initiated Outage | 00 Calm | 578 | 2014 | 339 | 120 Norman Road | CMPL 2019-05-23 10:44:00 by ETCHILD RMK: 342 PETREE RD TX ON GROUND FD ON SITE REQUIRED ETA CIRCUIT DID NOT HOLD----TARGETS AB FMAG 4789 | Overgrown primary on Petree Road in span between Mt Tabor Court & Gatehaven Rd behind 200L's/fault cascaded to backbone/found span faults @ 120 Norman Road/opened blades @ 39027189 to get circuit back on/cut tree limb from primary & restored blades; then opened 300amp doors @ 39076588 & downstream reclosers & 100T's to sectionalize before re-energizing/see events 11221806,11221446,11230811 & 11221807/count modified/issued WO 32806145 for tree work & 32831999 to change out pole & install 10' arms/skh9815 ~~~ 5/24/2019 ¦ skh9815 ¦ Work Order(s) Generated
131 | Dist | ELKIN sba8312 | SMITHTOWN - 29081201 | 5/23/2019 14:47 | 5/23/2019 15:50 | 11222301 | S-RCL - ABC Size: 560 WVE FID: 39007297 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P1 Pole, Creosote |  |  | F2 Forced Outage | 00 Calm | 535 | 1754 | 63 | Nebo & Forbush Rd 2624 Nebo Rd | RECLOSER LOCKED OUT..PER KENT..FREDDIE AWARE | Tractor trailer caught CATV line breaking pole, crew isolated damage by opening switches at regulators on event 11222411. Crew replaced pole 40/5 -45/4, Modified Customer count.... Pics on R&I Server 20190523-11222301-Smithtown Ret 29081201....WO# 33163161 to C/O Pole and add (3) 300 amp Solid doors ~~~ 5/24/2019 ¦ sba8312 ¦ Work Order(s) Generated
132 | Dist | ELKIN sba8312 | SMITHTOWN - 29081201 | 5/23/2019 17:08 | 5/23/2019 17:14 | 11222488 | S-RCL - ABC Size: 560 WVE FID: 39007297 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | 07 Proactive Work | 16 Closed Recl or Sectionalizer | P1 Pole, Creosote |  |  | P4 Crew Initiated Outage | 00 Calm | 535 | 1754 | 6 | Nebo Rd & Forbush Rd | DROPPED RECLOSER IN ORDER TO MAKE REGULATORS BACK HOT | Vehicle accident Tractor trailer caught CATV cable breaking pole crew sectionalized to isolate damage, related to event 11222411 Crew dropped RCL to close switches back in at Regulators ~~~ 5/24/2019 ¦ sba8312 ¦ Investigative Action
133 | Dist | Greensboro ELamb | COLFAX - 09502412 | 5/26/2019 03:56 | 5/26/2019 08:23 | 11225761 | S-CKT - ABC Size: Class 3 FID: 38356809 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA |  |  | P4 Crew Initiated Outage | 00 Calm | 1,610 | 1609 | 267 | 1363 Pleasant Ridge Rd | CKT DROPPED TO C/O POLE | ELamb: At 1363 Pleasant Ridge Rd, a 55/3 duke pole that held a double circuit line broke due to a car accident. The crew had to drop both Colfax 2410 for event 11225760 and Colfax 2412 for event 11225761. No follow up needed ~~~ 6/4/2019 ¦ ELamb ¦ Investigative Action
134 | Dist | Greensboro ELamb | JESSUPTOWN - 09072407 | 5/28/2019 12:40 | 5/28/2019 13:28 | 11227270 | S-CKT - ABC Size: Class 3 FID: 38356905 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | HR Reclose Block, fault occurred | 47 Replaced Pole | PP Pole |  |  | F2 Forced Outage | 00 Calm | 2,621 | 3382 | 48 | 4908 Lawndale Dr | keith minor riding out circuit - hit pole cotswold & lawndale see ev#11227330 / cleared pole & re-energized feeder | ELamb: Crew was working off of the back bone of Jessuptown 2407 and had circuit blocked for road widening project. Crew was not the cause of this outage. While circuit was blocked, a dump truck had his truck bed up and hook onto the primary causing the pole to break. The crew got the circuit back on by floating the pole insteading up opening up the upstream Viper Recloser faciliity id 168646957. No follow up needed ~~~ 5/29/2019 ¦ ELamb ¦ Investigative Action
135 | Dist | Eden gla4211 | LEAKSVILLE - 27100402 | 5/30/2019 06:15 | 5/30/2019 06:49 | 11229324 | S-CKT - ABC Size: Class 1A FID: 38359305 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | D1 Broken/Malfunctioning | 42 Replaced Crossarm/Brace | C1 Crossarm, Creosote |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 612 | 615 | 34 | 304 Morehead St | CIRCUIT OPENED TO REMOVE TREE OFF LINE APPROX 30 MIN - BRKN CROSS ARM AT 304 MOREHEAD - DBL CIRCUIT - MIKE SOMERS TREE CRW ASSISTING | G Akers .. circuit blinked several times. Linemen found broken crossarm at 304 Morehead St. Circuit was pulled off to replace crossarm. Tree was also overgrowing primary at 622 Taylor St. When circuit was pulled off crossarm was replaced and tree was trimmed. Different fault currents were recorded during blinks. ~~~ 5/31/2019 ¦ gla4211 ¦ Investigative Action
136 | Dist | Burlington jhp2990 | WHITSETT - 11202412 | 5/30/2019 14:14 | 5/30/2019 15:11 | 11229878 | S-CKT - ABC Size: Class 3 FID: 38374217 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA | PT PINE | 60 | F2 Forced Outage | 00 Calm | 920 | 920 | 57 | FUSE BLOWN AT FID FOH:51420876 | FEEDER LOCKOUT UNDER HLT - MARK KNOWLES RIDING LINE OUT...LOCKOUT TRIP INST 50 TARGET BG FMAG 2306 - found 50k fuse blown - techs riding it out to see where at | JHP2990: PIKE CREW WORKING ON VIPER INSTALLATION, HAD HLT ON CIRCUIT A 50K FUSE ID 51420876 BLEW, PINE TREE WITH ROOT ROTTEN/DEFECTIVE FELL JUST HITTING THE PRIMARY AND FELL TO THE GROUND. ON THE DIRT PORTION OF ABERNATHY ROAD CAUSING THE CIRCUIT OUTAGE. ~~~ 5/31/2019 ¦ jhp2990 ¦ Investigative Action
137 | Dist | KERNERSVILLE lmh9203 | SEDGE GARDEN - 03291207 | 5/31/2019 16:30 | 5/31/2019 22:19 | 11231560 | S-RCL - ABC Size: 800 VPSS FID: 39011743 | 02 Line Recloser | OH Distribution Line Overhead | EA Weather | D4 Burned/Exploded | 16 Closed Recl or Sectionalizer | 29 Conductor, bare |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 646 | 1770 | 349 | 566 LINVILLE RD | JUSTIN HAWKS (PIKE ) 336- 817 8515 RCL lockout FMAG 2561 911 ETA neeeded traffic lights out/office conducting traffic...Sedge Garden Rd and Kernersville Rd. CREW RODE OUT AND NO FAULT FOUND | LINE BURNED DOWN ~~~ 6/5/2019 ¦ lmh9203 ¦ Investigative Action
138 | Dist | LEWISVILLE skh9815 | HINSHAW BANK - 03151208 | 5/31/2019 17:56 | 5/31/2019 19:56 | 11231955 | S-CKT - ABC Size: Class 1A FID: 38349921 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | D1 Broken/Malfunctioning | M3 Copper | 30 Conductor, covered |  |  | F2 Forced Outage | 03 Wind | 579 | 2544 | 120 | 1ST STREET @ CLOVERDALE AVE | CMPL 2019-05-31 20:45:00 by ABJAMES RMK: Circuit lockout FMAG 5821 Targets BCG, Halos near 1530 W 1st near fac id 39160269 | MIDDLE PHASE COPPER PRIMARY BROKEN @ 1ST STREET & CLOVERDALE AVE/CREW SAID WIRE MAY HAVE HAD PRIOR DAMAGE/SEVERE THUNDERSTORM WITH WIND IN AREA/NO FU SKH9815 ~~~ 6/5/2019 ¦ skh9815 ¦ Investigative Action
139 | Dist | LEWISVILLE skh9815 | HINSHAW BANK - 03151208 | 5/31/2019 17:56 | 5/31/2019 23:43 | 11231961 | S-RCL - ABC Size: 560 WVE FID: 39008763 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | D1 Broken/Malfunctioning | M3 Copper | 30 Conductor, covered |  |  | F2 Forced Outage | 03 Wind | 1,735 | 2544 | 347 | LOCKLAND AVE & QUEEN ST | CMPL 2019-05-31 23:45:00 by ABJAMES RMK: RECLOSER LOCK OUT - ITR CHANGED TO 0100 06/01/19 | CREW FOUND 2 PHASES IN 2 DIFFERENT SPANS BROKEN AND ON THE GROUND/SEVERE THUNDERSTORM IN AREA ~~~ 6/3/2019 ¦ skh9815 ¦ Investigative Action
140 | Dist | Greensboro gla4211 | RUDD RET - 09262404 | 6/3/2019 15:05 | 6/3/2019 16:42 | 112347442 | S-CKT - ABC Size: Class 2 FID: 38372424 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 16 Accident, public vehicle | 39 Repaired Overhead Conductor | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 1,411 | 2663 | 97 | 3903 US 29 NORTH | 911 CONTACTED WITH 15 MIN ETA @1525: large tree down across power line. closest to 3903 us 29 n Greensboro nc -- 336-373-2222. police and fire on site./ABCG - FMAG 3256 | G Akers .. bulldozers clearing land pushed tree into circuit backbone. Wire was broken. Exact tree and location of tree is unknown. Land was cleared at time of investigation. No other work needed. ~~~ 6/5/2019 ¦ gla4211 ¦ Investigative Action
141 | Dist | KERNERSVILLE lmh9203 | FIDDLERS CRK - 03101210 | 6/7/2019 16:14 | 6/7/2019 17:25 | 11239496 | S-RCL - ABC Size: 800 VPSS FID: 385287765 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA |  |  | P4 Crew Initiated Outage | 02 Rain | 916 | 2188 | 71 | 1629 E SPRAGUE | CMPL 2019-06-07 17:36:00 by BWEVANS RMK: TECH NEEDED RECL OPENED FOR WIRE BURNING DROPPED RECL PER TECH..WIRE DOWN BURNING | AT 1629 E SPRAGUE, A CAR COLLIDED WITH ANOTHER CAR WHEN ENTERING THE INTERSECTION, PUSHING IT OFF THE ROADWAY INTO A UTILITY POLE. THE CAR CAUSED THE POLE TO SPLIT AND THE 1/0 CU CONDUCTORS TO GET TOGETHER AND BURN. THE RECLOSERS WERE OPENED TO MAKE THE SCENE SAFE. THE POLE WAS MADE STABLE UNTIL IT CAN BE CHANGED OUT. RECLOSERS PUT BACK TO NORMAL...lmh ~~~ 6/10/2019 ¦ lmh9203 ¦ Investigative Action
142 | Dist | HIGH POINT FAPlumm | E THMSVLE RT - 10151207 | 6/7/2019 18:28 | 6/7/2019 19:50 | 11239724 | S-CKT - ABC Size: Class 3 FID: 38354817 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M8 Creosote | P1 Pole, Creosote |  |  | F2 Forced Outage | 02 Rain | 1,037 | 1044 | 82 | VEHICLE ACCIDENT AT 101 PINEFIELD RD | JEFF MARSHALL 276 229 9219 BRAKER OPENED TO UNTANGLE BROKEN POLE TOP AFTER VEHICLE ACCIDENT AT 101 PINEFIELD RD | faplumm..A vehicle ran off the road at the entrance to Pinefield Townhomes and broke a 40/5. Crew asked for circuit to be dropped while they floated the conductor. Crew re-energized the circuit and proceeded to change out the pole. Pic's on server. ~~~ 6/10/2019 ¦ FAPlumm ¦ Investigative Action
143 | Dist | Greensboro ELamb | FRIENDSHIP - 09092406 | 6/7/2019 21:07 | 6/8/2019 00:07 | 11240001 | S-RCL - ABC Size: 800 VPST FID: 39007879 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | 25 Improper Installation | 52 Restored From Alternate Sourc | 43 Recloser, Electronic | G4 G&W Electric |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 892 | 2914 | 180 | 7108 W Friendly Ave | RECL LOCKOUT B C FAULT FMAG 3366 CAJ3396 - PER CALLER 7108 W FRIENDLY AVE SAW FIRE - FAILED RECLOSER - C DAVIS/W VERNON. DCC RESTORED BREAKER AND LEFT THE ETR BLANK | ELamb: At 7108 W Friendly Ave, the leads on the road side and middle phase of a newly installed Viper were laid up against each other and hole had burned through the insulators covers exposing the conductors causing a phase to phase fault. Equipment Inspector inspected the recloser bushing and everything look ok. No follow up needed. ~~~ 6/12/2019 ¦ ELamb ¦ Investigative Action
144 | Dist | RURAL HALL skh9815 | MT TABOR BNK - 03221205 | 6/9/2019 03:54 | 6/9/2019 04:30 | 11242845 | S-CKT - ABC Size: Class 1A FID: 38349825 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | 08 Error, Duke | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 02 Rain | 1,414 | 1414 | 36 | Mt Tabor Substation inside fence | voltage ok | Mt Tabor 1207 & 1208 locked out due to tree outside the row falling on OCB backbone/ C&M supervisor called grid for switching options/switching procedure was done to pick up Mt Tabor 1207 from Mt Tabor 1205/1205 locked out when switching was done/error in switching procedure and LO was over trip amp setting on breaker/see 11242024 & 11242025 also/no fu reqr skh9815 ~~~ 6/11/2019 ¦ skh9815 ¦ Investigative Action
145 | Dist | RURAL HALL skh9815 | BUXTON ST R - 03051214 | 6/13/2019 09:52 | 6/13/2019 11:04 | 11248892 | S-CKT - ABC Size: Class 1A FID: 38349251 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 14 Closed Breaker |  |  |  | F2 Forced Outage | 00 Calm | 1,476 | 1488 | 72 | unknown | CMPL 2019-06-13 11:09:00 by ASADDLE RMK: LOCKOUT UNDER HLT - RUNNING FAULT / ADAM GUNTER 336-756-6000 - TRIP INST 50 TARGET A G FMAG 1361 - POSSIBLE FAULT OFF COLISEUM DR BTWN PILGRIM CT & OLD TOWN CLUB RD - CREWS RODE OUT LINE & NO CAUSE FOUND/JLTADLO | Circuit blocked for crew working construction job/locked out on temporary fault/crew rode circuit and did not find problem/outage came in later that afternoo in fault current range for a tx off due to vines all over pole & tx/skh9815 ~~~ 6/14/2019 ¦ skh9815 ¦ Investigative Action
146 | Dist | Chapel Hill rlw2159 | JAMES ST - 19031207 | 6/13/2019 12:40 | 6/13/2019 18:12 | 11249610 | S-RCL - ABC Size: 560 WVE FID: 39008813 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | DC Insulation Failure | 16 Closed Recl or Sectionalizer | UG Cable, UG, 25KV 1/0 |  |  | F2 Forced Outage | 00 Calm | 633 | 2062 | 332 |  | CIRCUIT LOCKOUT TARGETS B-G FMAG 2217 ..TARGETS RESET ..FAULT HALOS W. POPLAR AVE BETWEEN BLACKWOOD AND LILAC....FAULT HALOS HILLSBOROUGH RD NEAR GREENSBORO RD... FAULT HALOS N. GREENSBORO RD NEAR OAK ST. | rlw2159--ckt outage 11249149 is related. Crew opened recloser to get circuit back on. re-energized once circuit was re-energized. Outage ticket 11249657 was the reason the blocked circuit went out. ~~~ 6/13/2019 ¦ rlw2159 ¦ Investigative Action
147 | Dist | Chapel Hill rlw2159 | JAMES ST - 19031207 | 6/13/2019 12:40 | 6/13/2019 18:10 | 11249609 | RCL - ABC Size: 200 L FID: 39008809 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | DC Insulation Failure | 16 Closed Recl or Sectionalizer | UG Cable, UG, 25KV 1/0 |  |  | F2 Forced Outage | 00 Calm | 728 | 2062 | 330 |  | CIRCUIT LOCKOUT TARGETS B-G FMAG 2217 ..TARGETS RESET ..FAULT HALOS W. POPLAR AVE BETWEEN BLACKWOOD AND LILAC....FAULT HALOS HILLSBOROUGH RD NEAR GREENSBORO RD... FAULT HALOS N. GREENSBORO RD NEAR OAK ST. | rlw2159--ckt outage 11249149 is related. Crew opened recloser to get circuit back on. re-energized once circuit was re-energized. The 100k fuse blew on Outage ticket 11249657 when this recloser was energized. This recloser was opened to get the circuit back on ticket# 11249149. ~~~ 6/18/2019 ¦ rlw2159 ¦ Investigative Action
148 | Dist | Chapel Hill rlw2159 | JAMES ST - 19031207 | 6/13/2019 12:40 | 6/13/2019 18:21 | 11249608 | RCL - ABC Size: 200 V4L FID: 39005368 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | DC Insulation Failure | 16 Closed Recl or Sectionalizer | UG Cable, UG, 25KV 1/0 |  |  | F2 Forced Outage | 00 Calm | 512 | 2062 | 341 |  | CIRCUIT LOCKOUT TARGETS B-G FMAG 2217 ..TARGETS RESET ..FAULT HALOS W. POPLAR AVE BETWEEN BLACKWOOD AND LILAC....FAULT HALOS HILLSBOROUGH RD NEAR GREENSBORO RD... FAULT HALOS N. GREENSBORO RD NEAR OAK ST. | rlw2159--ckt outage 11249149 is related. Crew opened recloser to get circuit back on. re-energized once circuit was re-energized. Outage ticket 11249657 was the reason the blocked circuit went out. ~~~ 6/13/2019 ¦ rlw2159 ¦ Investigative Action
149 | Dist | Greensboro ELamb | RANDOLPH - 09042410 | 6/15/2019 22:10 | 6/16/2019 03:20 | 11253860 | P3OH - ABC FID: 112932662 | 09 Jumper/wire cut/open | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | PP Pole |  |  | F2 Forced Outage | 00 Calm | 2,855 | 3907 | 310 | 707 E Florida St | RELIABILITY ENRG. MAKING OUTAGE CORRECTION. Customer count will be adjusted on 6/19/2019 | ELamb: At 707 E Florida St, a car in the pole hit a double circuit pole and causing Randolph 09042411 for event #11251125 and Randolph 09042410 for event # 11253869 to lockout. There were no switching opportunities for Randolph 09042411 for event #11251125. However, crew was able to close in a set of switches faciliity id 357651608 to tie Randolph 09042410 with Kildare 09082410 to restore 1,024 customers up to recloser facility id 39004559 for event #11250744. The Crew was able to cut a set of jumpers at facility id 112932662 for event #11253860 upstream from the recloser facility id 39004559 and installed temporary switches to restore an additional 2,855 customers leaving only 21 customers without power for the remainder of the outage. ~~~ 6/19/2019 ¦ ELamb ¦ Investigative Action
150 | Dist | Greensboro ELamb | RANDOLPH - 09042410 | 6/15/2019 22:10 | 6/16/2019 02:21 | 11250744 | S-RCL - XYZ Size: 560 WVE FID: 39004559 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | 16 Accident, public vehicle | 10 Automatic Restoration | PP Pole |  |  | F2 Forced Outage | 00 Calm | 1,024 | 3907 | 251 | 707 E Florida St | ETA 2240 CAR VS POLE 707 E FLORIDA ST. C HICKMANS CREWS REPLACED POLE 30', 40/5 POLE. JUST OUTSIDE STATION. FLAGGERS REQUESTED 2315 REF JT456568, BROKE 45/C DOUBLE CIRCUIT POLE, 8' WOOD ARM, 10' WOOD ARM, 8' FG ARM AND 6x336 SINGLE SIDE TIES. ARCOS ALT LIST CONTRACT SPEC SCOTTIE WILLIAMS CALLED 2355. ETA FOR CONTRACT CREWS IS 0100. | ELamb: At 707 E Florida St, a car in the pole hit a double circuit pole and causing Randolph 09042411 for event #11251125 and Randolph 09042410 for event # 11253869 to lockout. There were no switching opportunities for Randolph 09042411 for event #11251125. However, crew was able to close in a set of switches faciliity id 357651608 to tie Randolph 09042410 with Kildare 09082410 to restore 1,024 customers up to recloser facility id 39004559 for event #11250744. The Crew was able to cut a set of jumpers at facility id 112932662 for event #11253860 upstream from the recloser facility id 39004559 and installed temporary switches to restore an additional 2,855 customers leaving only 21 customers without power for the remainder of the outage. ~~~ 6/18/2019 ¦ ELamb ¦ Investigative Action
151 | Dist | Greensboro ELamb | RANDOLPH - 09042411 | 6/15/2019 22:10 | 6/16/2019 07:57 | 11251125 | S-CKT - ABC Size: Class 2 FID: 38374490 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | PP Pole |  |  | F2 Forced Outage | 00 Calm | 1,074 | 1075 | 587 | 707 E Florida St | ETA 2240 CAR VS POLE 707 E FLORIDA ST. C HICKMANS CREWS REPLACED POLE 30', 40/5 POLE. JUST OUTSIDE STATION. FLAGGERS REQUESTED 2315 REF JT456568, BROKE 45/C DOUBLE CIRCUIT POLE, 8' WOOD ARM, 10' WOOD ARM, 8' FG ARM AND 6x336 SINGLE SIDE TIES. ARCOS ALT LIST CONTRACT SPEC SCOTTIE WILLIAMS CALLED 2355. ETA FOR CONTRACT CREWS IS 0100. | ELamb: At 707 E Florida St, a car in the pole hit a double circuit pole and causing Randolph 09042411 for event #11251125 and Randolph 09042410 for event # 11253869 to lockout. There were no switching opportunities for Randolph 09042411 for event #11251125. ~~~ 6/18/2019 ¦ ELamb ¦ Investigative Action
152 | Dist | Greensboro ELamb | JESSUPTOWN - 09072409 | 6/16/2019 17:04 | 6/16/2019 17:40 | 11251467 | S-CKT - ABC Size: Class 3 FID: 38357313 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | 25 Improper Installation | 39 Repaired Overhead Conductor | 28 Other Equipment |  |  | P4 Crew Initiated Outage | 00 Calm | 4,224 | 4225 | 36 | 3207 Horse Pen Creek rd | EMERGENCY DROP - Line down. Across the road at intersection of horse pen creek rd and gray bluff ct - MECHANICAL JUMPER INSTALLED BY CONTACTORS WORKING ON LINE REROUTE BURNED DOWN. BLINK FMAG AC 3959 - POSSIBLE FAULT ON JESSUP GROVE RD BETWEEN TORY HILL DR AND HORSE PEN CREEK RD / ALSO DOWN HORSE PEN CREEK RD FROM JESSUP GROVE UP TO WALKING HORSE LN - BREAKER IS CLOSED BUT A PHASE DROPPED TO 28 AMPS FROM 280 | ELamb: At 3207 Horse Pen Creek Rd, a mechanical jumper was improperly installed causing it to fail and burn the line down that crosses over the main road so the crew had to drop the circuit. ~~~ 6/18/2019 ¦ ELamb ¦ Investigative Action
153 | Dist | Greensboro ELamb | JESSUPTOWN - 09072416 | 6/17/2019 11:24 | 6/17/2019 11:47 | 11251956 | S-CKT - ABC Size: Class 3 FID: 38357637 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | 30 Error, Duke Contractor | M2 ACSR | AU Splice, automatic |  |  | F2 Forced Outage | 00 Calm | 3,496 | 3496 | 23 | 1311 Fleming Rd S-RCL: 39011761 | LOCK OUT ON CIRCUIT TARGETS A-G FMAG 2336 ULCS CREW WORKING UNDER HLT JOHN MCMILLON 336 496 6845 SLEEVE PULLED APART CONTACT LINE CAME IN CONTACT WITH PRIMARY NO SWITHCING OR BACKFEEDING NEEDED OUTAGE LESS THAN 30 MIN. CREW TO CLEAR AND BE ABLE TO RESTORE IN APPROX 7 MIN...11:30 | ELamb: At 1311 Fleming Rd, Crew had the circuit block because they were changing out 4/0 primary to 556 primary under a GIP Project under work order 21166607. Crew was moving the field phase to the alley arms. The crew jack up the wire and removed the inlines and installed auto splice and then moved it over to the field phase alley arm, so they could pull in the new conductor. 30 minutes into the job the field phase slipped out of the auto splice because the primary was not seated in the auto splice correctly and because the circuit was block the circuit lockout. ~~~ 6/18/2019 ¦ ELamb ¦ Investigative Action
154 | Dist | ELKIN pmb4141 | ELKIN MAIN - 29011204 | 6/19/2019 18:02 | 6/19/2019 18:25 | 11255317 | S-CKT - ABC Size: Class 1A FID: 38351073 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | MP Porcelain | 38 Insulator | L3 Lapp |  | P4 Crew Initiated Outage | 00 Calm | 892 | 894 | 23 | COMMERCE ST AND S BRIDGE ST | EMERGENCY DROPPED CIRCUIT FOR KENT SUDDRETH REQUEST, BURNING WIRE ON CROSSARM, NO OTHER MEANS OF DISCONNECTS AVAILABLE, SEE EVENT 11255284.TWO BROKE INSULATORS DUE TO NATURAL DETERIATION. JUMPER LAID ON THE CROSSARM..REPAIRED AND CLOSED BREAKER | P. Butner: Two 1970 Lapp insulators broke on a DDE corner pole. A jumper was laying on the cross arm smoking (event-11255284). No switching was available and crew dropped circuit to replace the broken insulators. Pole is 6/10's mile from station. Circuit was put back to normal. Crew said the pole and cross arm was ok. Surrounding poles have already been replaced, no additional work needed. Pics on server ~~~ 6/20/2019 ¦ pmb4141 ¦ Investigative Action
155 | Dist | KERNERSVILLE lmh9203 | BROAD ST RET - 03411202 | 6/20/2019 04:30 | 6/20/2019 04:46 | 11255611 | S-CKT - ABC Size: Class 3 FID: 38350461 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M7 Penta | P3 Pole, Penta |  |  | P4 Crew Initiated Outage | 00 Calm | 971 | 974 | 16 | 1105 SILAS CREEK PKWY | Emergency drop due to car accident ... tx hang from pole and road blocked | AT 1105 SILAS CREEK PKWY, A VEHICLE WAS TRAVELING WEST ON SILAS CREEK PKWY WHEN IT RAN OFF THE ROAD TO THE RIGHT AND COLLIDED WITH AN AT&T UTILITY POLE. THE POLE BROKE AT GROUND UPON IMPACT. CREW HAD CKT DROPPED TO CLEAR ACCIDENT. DUKE REPLACED POLE....lmh......DANNY's RESPONSE AS TO WHY CREW DROPPED CKT, "This was an emergency, no time for hunting place to open. I am sure grid did not offer any info." ~~~ 6/21/2019 ¦ lmh9203 ¦ Investigative Action
156 | Dist - MED | Burlington jhp2990 | GLN RVN MN R - 11042412 | 6/20/2019 14:41 | 6/20/2019 17:01 | 11256901 | S-RCL - ABC Size: 800 VPST FID: 362856443 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | HR Reclose Block, fault occurred | D2 Dead | NA | PT PINE | 35 | F2 Forced Outage | 04 Wind, Rain and Lightning | 775 | 801 | 140 | 632 walker Rd | LANDEN CLAEYS 336 817 8515 RIDING OUT RECLOSER / AC TARGETS 3122 / POSS FAULT LOCATION BACK LOT BETWEEN RECL AND ELON OSSIPEE RD OR N WILLIAMSON AV TOWARD 3PH UG AT N OKELLY AV. Pike foreman found a tree on 3 phase at 632 walker Rd in Elon. | JHP2990:Dead pine tree fell on primary at 632 Walker Road taking out the recloser. Crew was changing out a pole at W Haggard Ave & Manning Ave. had HLT on Viper ID 362856443. Rapid approaching storm, crew was called about weather and were in the process of getting in the clear. Before they could get in the clear the storm hit. Switching was not done. ~~~ 6/25/2019 ¦ jhp2990 ¦ Investigative Action