## sample_outage_data
# | Category | Op Center | Circuit | Time Off | Time On | Outage ID | Device & Ph | Clearing Device | Resp. System | Cause (IEEE) | Failure Mode | AT/D/M | Eq. Code | Manuf./ Species | Cnt | Planned Outages | WE | # Cust | Ckt Cust | Dur | Fault Location | Crew Remarks | Additional Remarks
1 | Sub/T | Henderson i67431 | STALLINGS CROSSROADS 115KV - STALLINGS 23KV | 7/12/2018 15:02 | 7/12/2018 16:05 | 4741972 | SOURCE - ABC FID: T5302B01 | 01 Feeder Breaker/Recl in Substa | 00 Substation | 20 Equipment failure | DF | 53 Restored Transmission/Sub Pow | BR Relay | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 855 | 852 | 63 | Switch~T5302B01 | Transmission Substation Equipment Outage Feeder Circuit Breaker | DPW: On 7/12/18 at 15:02 HRS, the Stallings 23KV Feeder out of the Stallings 115KV Substation locked out due to a bad FCB. This impacted 855 customers off for 63 minutes. Total CMI Ã¢Â€Â“ 53,978. Investigation is ongoing..... ~~~ 7/13/2018 ¦ i67431 ¦ Investigative Action
2 | Sub/T | Raleigh DFontan | RALEIGH YONKERS ROAD 115KV - SUNNYBROOK ROAD 24KV | 8/27/2018 04:53 | 8/27/2018 07:10 | 4781383 | SOURCE - C FID: C837BJ_1240440 | 00 Substation device | 00 Substation | 20 Equipment failure | D1 Broken/Malfunctioning | 53 Restored Transmission/Sub Pow | 44 Regulator |  |  | F2 Forced Outage | 00 Calm | 785 | 1343 | 137 |  | Transmission Substation Equipment Outage Substation Regulator Regulator failed causing the breaker to lock out. | PEEL 8/27/18 - The C-phase voltage regulator in the Raleigh Yonkers Rd. 115 kV substation for the Sunnybrook Rd. 24 kV feeder catastrophically failed (the lid blew off & spewed oil all around the feeder exits area), and caused the FCB to lockout. The feeder was restored through switching over to the bank's transfer breaker. ~~~ 8/27/2018 ¦ DFontan ¦ Investigative Action
3 | Sub/T | Raleigh e68825 | RALEIGH YONKERS ROAD 115KV - SUNNYBROOK ROAD 24KV | 8/27/2018 04:53 | 8/27/2018 07:04 | 4781413 | SOURCE - ABC FID: T5126B11 | 00 Substation device | 00 Substation | 20 Equipment failure | D4 | 53 Restored Transmission/Sub Pow | 44 Regulator | H9 Howard | 11 | F2 Forced Outage | 00 Calm | 1588 | 1343 | 131 | Line~11M325_11M326_1670758 | Transmission Substation Equipment Outage Substation Regulator Regulator failed causing the breaker to lock out. | PEEL 8/27/18 - The C-phase voltage regulator in the Raleigh Yonkers Rd. 115 kV substation for the Sunnybrook Rd. 24 kV feeder catastrophically failed (the lid blew off & spewed oil all around the feeder exits area), and caused the FCB to lockout. The feeder was restored through switching over to the bank's transfer breaker. ~~~ 8/27/2018 ¦ e68825 ¦ Investigative Action
4 | Sub/T | Raleigh DFontan | RALEIGH YONKERS ROAD 115KV - SUNNYBROOK ROAD 24KV | 8/27/2018 04:55 | 8/27/2018 06:53 | 4781433 | SOURCE - C FID: 12PE40_1240222 | 00 Substation device | 00 Substation | 20 Equipment failure | D1 Broken/Malfunctioning | 53 Restored Transmission/Sub Pow | 44 Regulator |  |  | F2 Forced Outage | 00 Calm | 872 | 1343 | 118 |  | Transmission Substation Equipment Outage Substation Regulator Regulator failed causing the breaker to lock out. | PEEL 8/27/18 - The C-phase voltage regulator in the Raleigh Yonkers Rd. 115 kV substation for the Sunnybrook Rd. 24 kV feeder catastrophically failed (the lid blew off & spewed oil all around the feeder exits area), and caused the FCB to lockout. The feeder was restored through switching over to the bank's transfer breaker. ~~~ 8/28/2018 ¦ DFontan ¦ Investigative Action
5 | Sub/T | Raleigh DFontan | RALEIGH YONKERS ROAD 115KV - SUNNYBROOK ROAD 24KV | 8/27/2018 04:56 | 8/27/2018 06:53 | 4781432 | SOURCE - A FID: AE61BJ_1214939 | 00 Substation device | 00 Substation | 20 Equipment failure | D1 Broken/Malfunctioning | 53 Restored Transmission/Sub Pow | 44 Regulator |  |  | F2 Forced Outage | 00 Calm | 936 | 1343 | 117 |  | Transmission Substation Equipment Outage Substation Regulator Regulator failed causing the breaker to lock out. | PEEL 8/27/18 - The C-phase voltage regulator in the Raleigh Yonkers Rd. 115 kV substation for the Sunnybrook Rd. 24 kV feeder catastrophically failed (the lid blew off & spewed oil all around the feeder exits area), and caused the FCB to lockout. The feeder was restored through switching over to the bank's transfer breaker. ~~~ 8/27/2018 ¦ DFontan ¦ Investigative Action
6 | Sub/T | Raleigh DFontan | RALEIGH YONKERS ROAD 115KV - SUNNYBROOK ROAD 24KV | 8/27/2018 06:32 | 8/27/2018 06:53 | 4781375 | SOURCE - B FID: AE61BJ_1214939 | 00 Substation device | 00 Substation | 20 Equipment failure | D1 Broken/Malfunctioning | 53 Restored Transmission/Sub Pow | 44 Regulator |  |  | F2 Forced Outage | 00 Calm | 567 | 1343 | 21 |  | Transmission Substation Equipment Outage Substation Regulator Regulator failed causing the breaker to lock out. | PEEL 8/27/18 - The C-phase voltage regulator in the Raleigh Yonkers Rd. 115 kV substation for the Sunnybrook Rd. 24 kV feeder catastrophically failed (the lid blew off & spewed oil all around the feeder exits area), and caused the FCB to lockout. The feeder was restored through switching over to the bank's transfer breaker. ~~~ 8/27/2018 ¦ DFontan ¦ Investigative Action
7 | Sub/T | Raleigh DFontan | RALEIGH YONKERS ROAD 115KV - SUNNYBROOK ROAD 24KV | 8/27/2018 06:33 | 8/27/2018 06:53 | 4781387 | SOURCE - C FID: AE40BJ_1192076 | 00 Substation device | 00 Substation | 20 Equipment failure | D1 Broken/Malfunctioning | 53 Restored Transmission/Sub Pow | 44 Regulator |  |  | F2 Forced Outage | 00 Calm | 870 | 1343 | 20 |  | Transmission Substation Equipment Outage Substation Regulator Regulator failed causing the breaker to lock out. | PEEL 8/27/18 - The C-phase voltage regulator in the Raleigh Yonkers Rd. 115 kV substation for the Sunnybrook Rd. 24 kV feeder catastrophically failed (the lid blew off & spewed oil all around the feeder exits area), and caused the FCB to lockout. The feeder was restored through switching over to the bank's transfer breaker. ~~~ 8/27/2018 ¦ DFontan ¦ Investigative Action
8 | Sub/T - MED35 | Garner c72037 | RALEIGH WORTHDALE 230KV - GLENBROOK 23KV | 9/14/2018 01:10 | 9/14/2018 20:36 | 4830888 | SOURCE - ABC FID: T5168B04 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow | BU Bushing | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1605 | 1608 | 1166 | Switch~T5168B04 | Transmission Transmission Line Outage Unknown At Time Of Outage rode feeder out did not see and fault or problems | MHS- Line was patrolled and a tree was located that apparently fell onto the line between structures 22 and 23, this caused the line to burn into and break the poles and bent the arm on structure 23. Primary and BU relaying not working at Milburnie 230 caused remote relaying to operate on 115k and 230kv line and lockout both 1 & 2 Auto Bank 230/115kv Xfmrs. Primary bushing failed at Milburnie ~~~ 10/2/2018 (18 days) ¦ c72037 ¦ Investigative Action
9 | Sub/T - MED35 | Durham AArias | ENO - 14102401 | 9/14/2018 04:25 | 9/14/2018 07:02 | 10901391 | S-CKT - ABC Size: Class EX FID: 38355777 | 13 Distribution Source to Sub | 00 Substation | 28 Other Cause | D1 Broken/Malfunctioning | 37 Removed Limb or Tree From Lin | NA | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 938 | 938 | 157 | 3110 university station rd | CMPL 2018-09-14 07:02:00 by LEMCKIN RMK: POSSIBLE CIRCUIT BREAKER LOCK OUT | aarias// MED - hurricane in area. Per line crews, 44KV line inside substation having problems. Eno substation communications have been down since July. Have reached out to relay engineers, issue was resolved. They are looking into the possibility of having an alarm set up when communication is lost with the substations ~~~ 10/4/2018 (20 days) ¦ AArias ¦ Completion Codes or Remarks
10 | Sub/T - MED35 | Garner c72037 | RALEIGH WORTHDALE 230KV - PLAZA EAST 23KV | 9/14/2018 05:04 | 9/14/2018 19:00 | 4831871 | SOURCE - ABC FID: T5168B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow | BU Bushing | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1916 | 1789 | 836 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | MHS-MHS- Line was patrolled and a tree was located that apparently fell onto the line between structures 22 and 23, this caused the line to burn into and break the poles and bent the arm on structure 23. Primary and BU relaying not working at Milburnie 230 caused remote relaying to operate on 115k and 230kv line and lockout both 1 & 2 Auto Bank 230/115kv Xfmrs. Primary bushing failed at Milburnie ~~~ 10/2/2018 (18 days) ¦ c72037 ¦ Investigative Action
11 | Sub/T - MED35 | Garner c72037 | GARNER WHITE OAK 230KV - RAYNOR ROAD 24KV | 9/14/2018 05:47 | 9/15/2018 18:02 | 4831590 | SOURCE - ABC FID: T4730B12 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow | BU Bushing | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1438 | 1527 | 2175 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | MHS-MHS- Line was patrolled and a tree was located that apparently fell onto the line between structures 22 and 23, this caused the line to burn into and break the poles and bent the arm on structure 23. Primary and BU relaying not working at Milburnie 230 caused remote relaying to operate on 115k and 230kv line and lockout both 1 & 2 Auto Bank 230/115kv Xfmrs. Primary bushing failed at Milburnie ~~~ 10/2/2018 (17 days) ¦ c72037 ¦ Investigative Action
12 | Sub/T - MED35 | Garner c72037 | AUBURN 230KV - ROCK QUARRY ROAD 23KV | 9/14/2018 10:48 | 9/14/2018 20:45 | 4832624 | SOURCE - ABC FID: T4501B01 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow | BU Bushing | UU Unknown Manufacturer |  | F2 Forced Outage | 03 Wind | 1776 | 2669 | 597 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | MHS-MHS- Line was patrolled and a tree was located that apparently fell onto the line between structures 22 and 23, this caused the line to burn into and break the poles and bent the arm on structure 23. Primary and BU relaying not working at Milburnie 230 caused remote relaying to operate on 115k and 230kv line and lockout both 1 & 2 Auto Bank 230/115kv Xfmrs. Primary bushing failed at Milburnie ~~~ 10/2/2018 (18 days) ¦ c72037 ¦ Investigative Action
13 | Sub/T - MED35 | Garner c72037 | MILBURNIE 230KV - BELTLINE 23KV | 9/14/2018 12:10 | 9/14/2018 15:13 | 4826534 | OCB - ABC FID: T5000B44 | 00 Substation device | 00 Substation | 11 Unknown Cause | XX Event Exceeds Design | 27 Other/See Notes | NA | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1099 | 1100 | 183 |  | Missing Missing Missing | MHS-The line tripped to backup relaying due to extended tripping time at Milburnie Sub for a fault on the Erwin-Milburnie 230kV Line ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Completion Codes or Remarks
14 | Sub/T - MED35 | Garner c72037 | MILBURNIE 230KV - WILDERS GROVE 23KV | 9/14/2018 12:13 | 9/14/2018 15:13 | 4826519 | OCB - ABC FID: T5000B43 | 00 Substation device | 00 Substation | 11 Unknown Cause | D1 Broken/Malfunctioning | 53 Restored Transmission/Sub Pow | BR Relay | NA R | 0 | F2 Forced Outage | 12 Hurricane | 4200 | 2517 | 180 |  | Missing Missing Missing | MHS-The line tripped to backup relaying due to extended tripping time at Milburnie Sub for a fault on the Erwin-Milburnie 230kV Line ~~~ 10/22/2018 (38 days) ¦ c72037 ¦ Investigative Action
15 | Sub/T - MED35 | Garner omshistproc | AUBURN 230KV - MOUNT MORIAH 23KV | 9/14/2018 12:53 | 9/14/2018 20:45 | 4832101 | SOURCE - ABC FID: T4501B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 03 Wind | 554 | 1052 | 473 | Source~T4501 | Transmission Transmission Line Outage Unknown At Time Of Outage | ... NO OUTAGE REVIEW INFO
16 | Sub/T - MED35 | Asheboro omshistproc | BISCOE 115KV - BISCOE 23KV | 9/14/2018 14:24 | 9/16/2018 09:06 | 4844288 | SOURCE - ABC FID: T0990B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 03 Wind | 508 | 561 | 2562 | Switch~T0990B03 | Transmission Transmission Line Outage Unknown At Time Of Outage | ... NO OUTAGE REVIEW INFO
17 | Sub/T - MED35 | Garner c72037 | GARNER I-40 230KV - NEW HOPE 24KV | 9/14/2018 14:40 | 9/15/2018 19:50 | 4829400 | SOURCE - ABC FID: T4723B13 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow | BU Bushing | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 2635 | 2767 | 1750 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | MHS-MHS- Line was patrolled and a tree was located that apparently fell onto the line between structures 22 and 23, this caused the line to burn into and break the poles and bent the arm on structure 23. Primary and BU relaying not working at Milburnie 230 caused remote relaying to operate on 115k and 230kv line and lockout both 1 & 2 Auto Bank 230/115kv Xfmrs. Primary bushing failed at Milburnie ~~~ 10/2/2018 (17 days) ¦ c72037 ¦ Investigative Action
18 | Sub/T - MED35 | Garner c72037 | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 9/14/2018 15:56 | 9/14/2018 19:00 | 4831664 | SOURCE - ABC FID: T5168B01 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow | BU Bushing | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 2847 | 2861 | 184 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | MHS-MHS- Line was patrolled and a tree was located that apparently fell onto the line between structures 22 and 23, this caused the line to burn into and break the poles and bent the arm on structure 23. Primary and BU relaying not working at Milburnie 230 caused remote relaying to operate on 115k and 230kv line and lockout both 1 & 2 Auto Bank 230/115kv Xfmrs. Primary bushing failed at Milburnie ~~~ 10/2/2018 (18 days) ¦ c72037 ¦ Investigative Action
19 | Sub/T - MED35 | Raleigh e68825 | PINE LAKE 230KV - HIGHWAY 401 24KV | 9/14/2018 16:19 | 9/14/2018 20:32 | 4829975 | SOURCE - ABC FID: T5108B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 905 | 1584 | 253 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
20 | Sub/T - MED35 | Garner c72037 | RALEIGH WORTHDALE 230KV - ROSE LANE 23KV | 9/14/2018 17:22 | 9/14/2018 19:00 | 4830210 | SOURCE - ABC FID: T5168B02 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow | BU Bushing | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1820 | 1832 | 98 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | MHS-MHS- Line was patrolled and a tree was located that apparently fell onto the line between structures 22 and 23, this caused the line to burn into and break the poles and bent the arm on structure 23. Primary and BU relaying not working at Milburnie 230 caused remote relaying to operate on 115k and 230kv line and lockout both 1 & 2 Auto Bank 230/115kv Xfmrs. Primary bushing failed at Milburnie ~~~ 10/2/2018 (18 days) ¦ c72037 ¦ Investigative Action
21 | Sub/T - MED35 | Raleigh e68825 | RALEIGH FOXCROFT 230KV - SOUTH HALL 23KV | 9/14/2018 17:22 | 9/14/2018 20:39 | 4829777 | SOURCE - ABC FID: T4692B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 999 | 2742 | 197 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
22 | Sub/T - MED35 | Raleigh e68825 | RALEIGH HOMESTEAD 230KV - US 1 N 23KV | 9/14/2018 17:23 | 9/14/2018 20:14 | 4830765 | SOURCE - ABC FID: 17KW99_104281970 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 1484 | 2583 | 171 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
23 | Sub/T - MED35 | Raleigh e68825 | RALEIGH HOMESTEAD 230KV - WINDSOR FOREST 24KV | 9/14/2018 17:23 | 9/14/2018 19:59 | 4829596 | SOURCE - ABC FID: 15FQ22_103577922 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 1119 | 1097 | 156 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
24 | Sub/T - MED35 | Raleigh e68825 | RALEIGH EAST STREET 230KV - LONGVIEW 12KV | 9/14/2018 17:23 | 9/14/2018 21:31 | 4829376 | SOURCE - ABC FID: T5120B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 881 | 892 | 248 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
25 | Sub/T - MED35 | Raleigh e68825 | PINE LAKE 230KV - FOX ROAD 24KV | 9/14/2018 17:23 | 9/14/2018 20:35 | 4831656 | SOURCE - ABC FID: T5108B14 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 2359 | 1749 | 192 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
26 | Sub/T - MED35 | Raleigh e68825 | RALEIGH FOXCROFT 230KV - RALEIGH FOXCROFT BUFFALOE ROAD 23KV | 9/14/2018 17:23 | 9/14/2018 21:49 | 4831432 | SOURCE - ABC FID: T4692B01 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 2899 | 2910 | 266 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
27 | Sub/T - MED35 | Raleigh e68825 | RALEIGH FOXCROFT 230KV - JANE LANE 23KV | 9/14/2018 17:23 | 9/14/2018 20:32 | 4832196 | SOURCE - ABC FID: T4692B02 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 2962 | 2960 | 189 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
28 | Sub/T - MED35 | Raleigh e68825 | PINE LAKE 230KV - WAKE FOREST 24KV | 9/14/2018 17:23 | 9/14/2018 20:36 | 4832475 | SOURCE - ABC FID: T5108B04 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 1116 | 1062 | 193 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
29 | Sub/T - MED35 | Raleigh e68825 | PINE LAKE 230KV - GREEN ROAD 24KV | 9/14/2018 17:23 | 9/14/2018 20:38 | 4831321 | SOURCE - ABC FID: T5108B06 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 2480 | 2476 | 195 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
30 | Sub/T - MED35 | Raleigh e68825 | RALEIGH EAST STREET 230KV - EAST STREET 12KV | 9/14/2018 17:23 | 9/14/2018 21:26 | 4832100 | SOURCE - ABC FID: T5120B02 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 847 | 852 | 243 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
31 | Sub/T - MED35 | Zebulon i70604 | KNIGHTDALE SQUARE D 230KV - WIDEWATERS 24KV | 9/14/2018 17:23 | 9/14/2018 17:35 | 4829949 | SOURCE - ABC FID: T4852B12 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 03 Wind | 1130 | 1215 | 12 | Load~ADB22Q | Transmission Transmission Line Outage Unknown At Time Of Outage transmission line outage transmission line outage | CPS// Verified customer count and breaker outage time // Full review pending transmission review ~~~ 9/24/2018 ¦ i70604 ¦ Modeling
32 | Sub/T - MED35 | Zebulon i70604 | KNIGHTDALE SQUARE D 230KV - MIDWAY 24KV | 9/14/2018 17:23 | 9/14/2018 17:35 | 4829632-1 | SOURCE - ABC FID: T4852B13 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 03 Wind | 1435 | 1652 | 12 | Switch~T4852B13 | Transmission Transmission Line Outage Unknown At Time Of Outage transmission line outage transmission line outage | CPS// Verified customer count and breaker outage time // Full review pending transmission review ~~~ 9/24/2018 ¦ i70604 ¦ Modeling
33 | Sub/T - MED35 | Zebulon i70604 | ROLESVILLE 230KV - WATKINS ROAD 24KV | 9/14/2018 17:23 | 9/14/2018 17:35 | 4832531 | SOURCE - ABC FID: T5205B01 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 02 Rain | 1995 | 2097 | 12 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | CPS// Verified customer count and breaker outage time // Full review pending transmission review ~~~ 9/24/2018 ¦ i70604 ¦ Modeling
34 | Sub/T - MED35 | Zebulon i70604 | ROLESVILLE 230KV - ROLESVILLE 24KV | 9/14/2018 17:23 | 9/14/2018 17:35 | 4831671 | SOURCE - ABC FID: T5205B12 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 02 Rain | 1725 | 2160 | 12 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | CPS// Verified customer count and breaker outage time // Full review pending transmission review ~~~ 9/24/2018 ¦ i70604 ¦ Modeling
35 | Sub/T - MED35 | Zebulon i70604 | ROLESVILLE 230KV - MITCHELL MILL 24KV | 9/14/2018 17:23 | 9/14/2018 17:35 | 4830034 | SOURCE - ABC FID: T5205B04 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 02 Rain | 1,039 Cust Eq: 916 | 1958 | 12 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | CPS// Verified customer count and breaker outage time // Full review pending transmission review // Please note: 916 customers were saved by the self healing team with the Perry Creek Feeder ~~~ 9/24/2018 ¦ i70604 ¦ Modeling
36 | Sub/T - MED35 | Zebulon i70604 | ROLESVILLE 230KV - WAKE CROSSROADS 24KV | 9/14/2018 17:23 | 9/14/2018 17:35 | 4830162 | SOURCE - ABC FID: T5205B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 00 Calm | 1909 | 1992 | 12 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | CPS// Verified customer count and breaker outage time // Full review pending transmission review ~~~ 9/24/2018 ¦ i70604 ¦ Modeling
37 | Sub/T - MED35 | Zebulon omshistproc | ROLESVILLE 230KV - HOPKINS 24KV | 9/14/2018 17:23 | 9/14/2018 18:31 | 4830847 | SOURCE - ABC FID: T5205B02 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 02 Rain | 740 | 2046 | 68 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | ... NO OUTAGE REVIEW INFO
38 | Sub/T - MED35 | Raleigh e68825 | PINE LAKE 230KV - BOULEVARD CENTER 24V | 9/14/2018 17:25 | 9/14/2018 20:29 | 4831200 | SOURCE - ABC FID: T5108B01 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 722 | 723 | 184 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
39 | Sub/T - MED35 | Raleigh e68825 | RALEIGH EAST STREET 230KV - SOUTH STREET 12KV | 9/14/2018 17:27 | 9/14/2018 21:31 | 4832733 | SOURCE - ABC FID: T5120B04 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 502 | 503 | 244 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
40 | Sub/T - MED35 | Raleigh e68825 | RALEIGH EAST STREET 230KV - PERSON STREET 12KV | 9/14/2018 17:28 | 9/14/2018 21:27 | 4831390 | SOURCE - ABC FID: T5120B07 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 725 | 731 | 239 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
41 | Sub/T - MED35 | Raleigh e68825 | FALLS 230KV - RICHLAND CREEK 24KV | 9/14/2018 17:32 | 9/14/2018 20:02 | 4830840 | SOURCE - ABC FID: 10QW52_1667696 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 1594 | 1860 | 150 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
42 | Sub/T - MED35 | Raleigh e68825 | RALEIGH EAST STREET 230KV - BILTMORE HILLS 12KV | 9/14/2018 18:59 | 9/14/2018 21:29 | 4832808 | SOURCE - ABC FID: T5120B05 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 969 | 968 | 150 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
43 | Sub/T - MED35 | Raleigh e68825 | RALEIGH EAST STREET 230KV - LENOIR STREET 12KV | 9/14/2018 19:00 | 9/14/2018 21:28 | 4831973 | SOURCE - ABC FID: T5120B06 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 41 Loss of transmission/generati | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 12 Hurricane | 1197 | 1201 | 148 |  | Transmission Transmission Line Outage Unknown At Time Of Outage | PEEL 9/27/18: Transmission personnel are still studying to determine the cause of this outage. ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
44 | Sub/T - MED35 | Asheboro omshistproc | BISCOE 115KV - STAR NORTH 23KV | 9/14/2018 19:25 | 9/16/2018 09:06 | 4844312 | SOURCE - ABC FID: T0990B01 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 03 Wind | 943 | 1011 | 2261 | Switch~T0990B01 | Transmission Transmission Line Outage Unknown At Time Of Outage | ... NO OUTAGE REVIEW INFO
45 | Sub/T | Raleigh e68825 | RALEIGH LEESVILLE ROAD 230KV - GLENDOWER 24KV | 9/29/2018 13:26 | 9/29/2018 14:29 | 4873224-2 | SOURCE - ABC FID: T4910B29 | 01 Feeder Breaker/Recl in Substa | 00 Substation | 20 Equipment failure | 04 Wildlife | 56 Sectionalized/Restored Servic | 44 Regulator |  | 10 | F2 Forced Outage | 00 Calm | 1,360 Cust Eq: 1288 | 2761 | 63 | Switch~T4910B21 | Transmission Substation Equipment Outage Substation Regulator BAD A PHASE REGULATOR | PEEL 10/2/18: The A-phase Glendower Feeder single phase regulator in the Leesville Rd. Substation failed (exploded, top seal ruptured, oil caught fire & burned two of the units), and locked out the Glendower FCB at 1:26 PM. The SHT # 78 operated (RCL 15B416 opened, & the tie RCL 15A796 closed at 1:29:03 PM restoring 1288 customers). The Responding crew isolated (bypassed) all 3 feeder regulators, and then had DCC remotely close the FCB at 2:29:13 PM, restoring the remaining 1360 customers. ~~~ 10/2/2018 ¦ e68825 ¦ Investigative Action
46 | Sub/T | Chatham County omshistproc | BYNUM 230KV - FEARRINGTON 24KV | 9/30/2018 22:06 | 9/30/2018 23:58 | 4873846 | SOURCE - ABC FID: T1025B12 | 00 Substation device | 00 Substation | 20 Equipment failure | D1 Broken/Malfunctioning | 53 Restored Transmission/Sub Pow | CS Circuit Switcher |  |  | F2 Forced Outage | 00 Calm | 1892 | 1897 | 112 |  | Transmission Substation Equipment Outage High-Side Switch | ... NO OUTAGE REVIEW INFO
47 | Sub/T | Chatham County omshistproc | BYNUM 230KV - CHAPEL HILL 23KV | 9/30/2018 22:07 | 9/30/2018 23:58 | 4873657 | SOURCE - ABC FID: T1025B01 | 00 Substation device | 00 Substation | 20 Equipment failure | D1 Broken/Malfunctioning | 53 Restored Transmission/Sub Pow | CS Circuit Switcher |  |  | F2 Forced Outage | 00 Calm | 2315 | 2307 | 111 |  | Transmission Substation Equipment Outage High-Side Switch | ... NO OUTAGE REVIEW INFO
48 | Sub/T - MED35 | Asheboro omshistproc | BISCOE 115KV - BISCOE 23KV | 10/11/2018 15:35 | 10/11/2018 16:13 | 4881579 | SOURCE - ABC FID: T0990B03 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 02 Rain | 561 | 561 | 38 | Switch~T0990B03 | Transmission Transmission Line Outage Unknown At Time Of Outage | ... NO OUTAGE REVIEW INFO
49 | Sub/T - MED35 | Asheboro omshistproc | BISCOE 115KV - STAR NORTH 23KV | 10/11/2018 15:36 | 10/11/2018 16:16 | 4881722 | SOURCE - ABC FID: T0990B01 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 02 Rain | 1015 | 1011 | 40 | Switch~T0990B01 | Transmission Transmission Line Outage Unknown At Time Of Outage UNKOWN | ... NO OUTAGE REVIEW INFO
50 | Sub/T - MED35 | Asheboro omshistproc | BISCOE 115KV - HIGHWAY 220 23KV | 10/11/2018 15:36 | 10/11/2018 16:14 | 4881602 | SOURCE - ABC FID: T0990B02 | 11 Transmission device | 11 Transmission | 41 Loss of transmsn/generation | 11 Unknown Cause | 53 Restored Transmission/Sub Pow |  |  |  | F2 Forced Outage | 02 Rain | 894 | 898 | 38 | Node~T0990B02_1 | Transmission Transmission Line Outage Unknown At Time Of Outage UNKOWN | ... NO OUTAGE REVIEW INFO
51 | Sub/T - MED35 | Durham AArias | ENO - 14102401 | 10/11/2018 16:44 | 10/12/2018 14:22 | 10955647 | S-CKT - ABC Size: Class EX FID: 38355777 | 11 Transmission device | 11 Transmission | 03 Vegetation | 03 Tree (Vegetation) | 14 Closed Breaker | NA | NA R |  | F2 Forced Outage | 12 Hurricane | 831 | 938 | 1298 | various | CMPL 2018-10-12 14:22:00 by LWG9380 RMK: POSS CIR OUTAGE-ENO RET 2401 | aarias// MED - hurricane. Transmission issue. Per the transmission report: "Relays and breaker operated correctly for all 4 faults. All faults were A-C, with the second fault evolving to a three phase fault before clearing. The Chapel Hill automatic sectionalizing switch failed to operate automatically for this event. Based on the data it appears to be an issue with the current measurement devices (CMDIIÂ¿s). Sectionalizing switch was opened remotely from ECC and Eno Retail was restored once the fault location was provided. Patrol findings were a tree near structure 107. Cross arm and insulator were replaced. Field finding: Tree on line near Structure#107. Replaced cross arm and insulator" ~~~ 10/22/2018 ¦ AArias ¦ Completion Codes or Remarks
52 | Sub/T - MED35 | Durham AArias | ENO - 14102403 | 10/11/2018 16:44 | 10/12/2018 16:21 | 10955643 | S-CKT - ABC Size: Class 3 FID: 38374965 | 11 Transmission device | 11 Transmission | 03 Vegetation | 03 Tree (Vegetation) | 14 Closed Breaker | NA | NA R |  | F2 Forced Outage | 12 Hurricane | 1556 | 1560 | 1417 | aarias// transmission structure | CUSTOMER STATES THAT THERE IS A POLE AND TX DOWN BESIDE THERE HOUSE MCARTHY | aarias// MED - hurricane. Transmission issue. Per the transmission report: "Relays and breaker operated correctly for all 4 faults. All faults were A-C, with the second fault evolving to a three phase fault before clearing. The Chapel Hill automatic sectionalizing switch failed to operate automatically for this event. Based on the data it appears to be an issue with the current measurement devices (CMDIIÂ¿s). Sectionalizing switch was opened remotely from ECC and Eno Retail was restored once the fault location was provided. Patrol findings were a tree near structure 107. Cross arm and insulator were replaced. Field finding: Tree on line near Structure#107. Replaced cross arm and insulator" ~~~ 10/18/2018 ¦ AArias ¦ Completion Codes or Remarks
53 | Sub/T - MED35 | Durham dlm4375 | OXFORD ROAD - 14091206 | 10/11/2018 16:57 | 10/12/2018 12:14 | 10956201 | S-CKT - ABC Size: Class 1A FID: 38356125 | 01 Feeder Breaker/Recl in Substa | 00 Substation | 11 Unknown Cause | HZ Cause undetermined | 14 Closed Breaker | 29 Conductor, bare |  |  | F2 Forced Outage | 12 Hurricane | 592 | 594 | 1157 | unknown | CMPL 2018-10-12 13:38:00 by BJACOBY RMK: Circuit outage, no phone calls on Hazards | rlw2159-MED DAY-HURRICANE MICHAEL-circuit outage crews rode out and found nothing tried circuit and held. ~~~ 10/23/2018 ¦ dlm4375 ¦ Completion Codes or Remarks
54 | Sub/T - MED | Chapel Hill AArias | WHITE CROSS - 19051203 | 10/12/2018 14:25 | 10/12/2018 17:28 | 10968016 | S-CKT - ABC Size: Class 3 FID: 38358525 | 11 Transmission device | 11 Transmission | 28 Other Cause | HZ Cause undetermined | 14 Closed Breaker | NA | NA R |  | F2 Forced Outage | 12 Hurricane | 876 | 930 | 183 |  | white cross transmission lines returned back to normal, circuit restored | aarias// MED - hurricane in area. Transmission outage ~~~ 10/22/2018 ¦ AArias ¦ Completion Codes or Remarks
55 | Veg | Raleigh DFontan | MORDECAI 115KV - BISHOPS PARK 12KV | 7/6/2018 19:32 | 7/6/2018 20:04 | 4738670 | OCB - ABC FID: T5005B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | LH Tree limb, overhang | DN No apparent defect | NA | OA Oak | 5 | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 1620 | 1627 | 32 | Switch~T5005B05 | Overhead Fac Overhead Primary Failure (No Tree Involved) Splice Failed 477 sleeve pulled out during storm. | PEEL 7/11/18: Crew-initiated outage to safely clear an oak limb that had fallen on the Cleveland St. 12 kV feeder in double circuit span RDH69-RDH70. Responding C&M Crew had DCC remotely open the FCB at 19:32, then had them close in the FCB at 20:04 after the tree limb was cleared from the line. ~~~ 7/11/2018 ¦ DFontan ¦ Investigative Action
56 | Veg | Raleigh DFontan | MORDECAI 115KV - CLEVELAND STREET 12KV | 7/6/2018 19:36 | 7/6/2018 20:04 | 4738508 | OCB - ABC FID: T5005B06 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | NA | OA Oak | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1320 | 1352 | 28 | RDH69-RDH70 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE ON FEEDER AT DIS # RDH70 | PEEL 7/11/18: A 6" x ~25' long live limb, 5' off of the line CL, during a thunderstorm, broke off of a 3' diam. x ~70' tall Oak, 12' off of the line CL, laid on the Cleveland St. feeder in double circuit (with the Bishops Park 12 kV feeder) span RDH69-RDH70, and locked out the FCB. Responding C&M Techs had DCC remotely open the Bishops Park 12kV FCB to de-energize the circuit to enable them to safely clear the hanging limb, then had DCC remotely close in both FCBs (at 20:04 & 20:05) to restore service to both feeders. ~~~ 7/11/2018 ¦ DFontan ¦ Investigative Action
57 | Veg | Durham dlm4375 | GREEN STREET - 14121202 | 7/11/2018 14:38 | 7/11/2018 17:47 | 10824124 | SOH - ABC Size: 600 Line Disconnect FID: 39035370 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | CR Crossarm | PV Pine, Virginia | 70 | F2 Forced Outage | 00 Calm | 628 | 1210 | 189 | TREE ON LINE BURNING AT 723 ANDERSON ROAD | TREE ON LINE BURNING AT 713 ANDERSON ROAD NEAR- CORNER WITH DUKE UNIVERISTY ROAD. TARGETS ABC FAULT MAG-3309. TL133/UMBEHANT. CLOSED BREAKER AND OPENED SOLID BLADE TO ISOLATE | dlm4375 a defective Virginia Pine 70' uprooted due to environmental issues roots were right on top of ground no root system(top heavy)fell & laid on ohd pri on dbl cirt. Dbl cir Green St 1201 & Green St 1202. Green St 1201 is self healing w/HV 1204 see 108239421.Tree fell across from 723 Anderson Av 2 spans past rec facid 398753895 on green 1201.Green 1201opened isolated swtchs on viper rec facid 398753895 see 108239422 to get cir on. green1201 see 10823943 opened up due to wire slapping together one span before the rec, self healing couldnt operate correctly because self healing assumed there was 2 faults (no cust saved) . On Green St 1202 cir locked out see 10823943, crews opened 600amp inlines see 10824124 facid 39035370 at Yearby Av isolate to get cir back on. Duke Crews/Tree crews cut/rmvd tree. Duke crews rmvd dbl set of xarms on dbl cir pole that was titled&replaced w/single FG xarm, pole less than 11 degree angle. retied insuls. fusee WR#29212503 for next pole down where tree fell to c/o xarm, c/o ins ~~~ 7/11/2018 ¦ dlm4375 ¦ Work Order(s) Generated
58 | Veg | Durham dlm4375 | GREEN STREET - 14121202 | 7/11/2018 14:38 | 7/11/2018 15:51 | 10823941 | S-CKT - ABC Size: Class 1A FID: 38356185 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | CR Crossarm | PV Pine, Virginia | 70 | F2 Forced Outage | 00 Calm | 577 | 1210 | 73 | TREE ON LINE BURNING AT 713 ANDERSON ROAD | TREE ON LINE BURNING AT 713 ANDERSON ROAD NEAR- CORNER WITH DUKE UNIVERISTY ROAD. TARGETS ABC FAULT MAG-3309. TL133/UMBEHANT. OPENED SOLID BLADE 39035370 AND CLOSED BREAKER TO ISOLATE FOR REPAIRS. | dlm4375 a defective Virginia Pine 70' uprooted due to environmental issues roots were right on top of ground no root system(top heavy)fell & laid on ohd pri on dbl cirt. Dbl cir Green St 1201 & Green St 1202. Green St 1201 is self healing w/HV 1204 see 108239421.Tree fell across from 723 Anderson Av 2 spans past rec facid 398753895 on green 1201.Green 1201opened isolated swtchs on viper rec facid 398753895 see 108239422 to get cir on. green1201 see 10823943 opened up due to wire slapping together one span before the rec, self healing couldnt operate correctly because self healing assumed there was 2 faults (no cust saved) . On Green St 1202 cir locked out see 10823943, crews opened 600amp inlines see 10824124 facid 39035370 at Yearby Av isolate to get cir back on. Duke Crews/Tree crews cut/rmvd tree. Duke crews rmvd dbl set of xarms on dbl cir pole that was titled&replaced w/single FG xarm, pole less than 11 degree angle. retied insuls. fusee WR#29212503 for next pole down where tree fell to c/o xarm, c/o ins ~~~ 7/11/2018 ¦ dlm4375 ¦ Work Order(s) Generated
59 | Veg | Chatham County omshistproc | PITTSBORO 230KV - PITTSBORO 23KV | 7/17/2018 03:44 | 7/17/2018 05:11 | 4744255 | RECLOSER - B FID: BS21AF_115172539 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 00 Calm | 528 | 2163 | 86 | Line~AW72AF_AW74AF_2453046 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
60 | Veg | Garner c72037 | HOLLY SPRINGS 230KV - SURRY RIDGE 24KV | 7/22/2018 05:22 | 7/22/2018 06:54 | 4747763 | OCB - ABC FID: T4795B22 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect | NA | PT PINE | 21 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1404 | 1400 | 92 | U848BH | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | MHS- On Sunday July 22, the Surry Ridge feeder locked out at 5:22 am. Crew rode line out finding Some Pine and Pin Oak tree limbs 21' from C/L growing and hanging all over the feeder. there were signs of previous burning. Crew set up and trimmed trees back. Then had DCC hot feeder back up. ~~~ 7/26/2018 ¦ c72037 ¦ Investigative Action
61 | Veg | Garner c72037 | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 7/22/2018 06:33 | 7/22/2018 07:31 | 4747829 | OCB - ABC FID: T5168B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | OB Oak, white | 35 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2840 | 2861 | 58 | Line~17GC74_RED13_104192796 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell into primary at RED13-17GC76. removed tree. kv tree fell into primary at RED13-17GC76. removed tree. kv | MHS- on Sunday July 22, the Little John Feeder locked out at 6:33 am. The crew rode the line out and found a live white oak tree 35' from C/L broke off at ground level, falling across all 3 phases . Crew set up and cut tree from lines. then had DCC hot the feeder back up. no damage to our equipment ~~~ 7/26/2018 ¦ c72037 ¦ Investigative Action
62 | Veg | Durham AArias | POPE ROAD - 14082410 | 7/22/2018 08:50 | 7/22/2018 11:49 | 10836349 | S-RCL - ABC Size: 800 VPTT FID: 410841375 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LD Tree limb, dead | D2 Dead | NA | UN Unknown Species |  | F2 Forced Outage | 00 Calm | 1699 | 2079 | 179 | pickett and mcdowell rd | CMPL 2018-07-22 11:50:00 by WJAMES RMK: TL510/Toby Garner and TL518/Bill James....RCL off. Self Healing did not reconfigure. | aarias// per Bill James, small dead limb burned off across two phases of primary at Pickett and McDowell Rd, took out recloser. Area closely inspected, could not pinpoint source. Self healing did not reconfigure. Issue communicated to DPAC, upon investigation the following was discovered: 1. RECL410862847 is designed to be in Switch Mode, Group5, but is currently programmed as a Recloser in Group4. 2. RECL410781226 and RECL410862847 have the same settings, which explains the mis-coordination. 3. RECL410841375 is a sectionalizer with 2 counts to lockout (as designed) and RECL410892867 is a sectionalizer with 3 counts to lockout. This explains why RECL410841375 opened first. DPAC will take care of configuring the devices properly to eliminate further coordination issues ~~~ 7/24/2018 ¦ AArias ¦ Investigative Action
63 | Veg | Zebulon i70604 | SPRING HOPE 115KV - TAYLORS CROSSROADS 23KV | 7/22/2018 17:17 | 7/22/2018 18:34 | 4748262-2 | SWITCH - ABC FID: EB37BC_1944088 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | DC Internal stem decay | NA | SY Sycamore | 31 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1170 | 2058 | 77 | EC04BC | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | CPS// During severe thunderstorm the top of a 75' sycamore tree broke and fell over on to the conductor at dis#EC04BC causing G&W recloser D931BC to open. Line tech opened air break switch EB37BC to isolate fault then closed G&W D931BC (step 1). Line techs trimmed tree top off of conductor and closed air break switch EB37BC restoring all remaining customers (step 2). The base of the tree was 31' from center line. No damage to equipment. ~~~ 7/25/2018 ¦ i70604 ¦ Investigative Action
64 | Veg | Zebulon i70604 | SAMARIA 115KV - SAMARIA 24KV | 7/22/2018 17:26 | 7/22/2018 18:06 | 4748265-1 | RECLOSER - AC FID: ZLF09_104347073 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | SZ Sweet Gum |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 515 | 1803 | 40 | ZLC51 | Tree/Vegetatn Limb Fell from Outside Right of Way None limb on line at zlc51 limb on line at zlc51 | CPS//During severe thunderstorm a 5' sweet gum limb broke and fell across A&C phase at dis#ZLC51 causing both phases to open at G&W recloser ZLF09. Tree was located outside of R/W. Unable to determine exact location on tree where limb broke out from. No damage to equipment and no apparent defect on limb. Responding line tech cleared limb from line and all lights were restored. ~~~ 7/24/2018 ¦ i70604 ¦ Investigative Action
65 | Veg | Chatham County omshistproc | SILER CITY 115KV - ROCKY RIVER 24KV | 7/22/2018 19:16 | 7/22/2018 20:09 | 4748328 | RECLOSER - BC FID: 6HV05_104617066 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 742 | 1689 | 52 | Recloser~6HV05_104617066 | Tree/Vegetatn Tree/Limb Growth None CLOSED IN RECLOSER | ... NO OUTAGE REVIEW INFO
66 | Veg | Chapel Hill AArias | EASTGATE RET - 19021209 | 7/22/2018 21:30 | 7/23/2018 00:29 | 10837514 | S-RCL - ABC Size: 560 WVE FID: 39006161 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LX Trees, overgrown primary | DN No apparent defect | NA | EV Evergreen | 0 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1053 | 1262 | 179 | aarias// behind 40 Hamilton Rd | LOCKOUT with targets a to b and fmag 2288 | aarias// live overgrown evergreen burning across primary in backlot backbone. Recommended adding ckt to trim list for 2019 ~~~ 7/24/2018 ¦ AArias ¦ Investigative Action
67 | Veg | Raleigh e68825 | METHOD 230KV - BUDLEIGH 12KV | 7/23/2018 15:50 | 7/23/2018 16:40 | 4749216-1 | OCB - ABC FID: T4990B37 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | 38 Insulator | OA Oak | 3 | F2 Forced Outage | 00 Calm | 1078 | 1067 | 50 | Load~FQ91BL | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | Peel/Fontana 7/24/18: A 4" dia. x ~17' long live limb, 3' horizontal from the line CL, broke off of the overhang a 3' dia. x ~70' tall Pin Oak, fell onto the feeder primary conductors at pole FQ91BL, and locked out the FCB. The tree is leaning towards the feeder and overhanging the feeder, and we consider it a "Danger Tree", therefore we are requesting Veg. Management to have this tree removed (It has taken this feeder out earlier this year (3'18/2018, Outage # 4688580). ~~~ 7/24/2018 ¦ DFontan ¦ Vegetation Management
68 | Veg | Chatham County omshistproc | PITTSBORO 230KV - NORTHWOOD 23KV | 7/23/2018 16:15 | 7/23/2018 17:21 | 4749236-2 | OCB - ABC FID: T2250B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 752 | 2180 | 66 | Node~5980602 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree leaned over into feeder at BG13AF tree leaned over into feeder at BG13AF | ... NO OUTAGE REVIEW INFO
69 | Veg | Chatham County omshistproc | PITTSBORO 230KV - NORTHWOOD 23KV | 7/24/2018 08:35 | 7/24/2018 09:04 | 4749721-2 | OCB - ABC FID: T2250B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 02 Rain | 753 | 2180 | 29 | Load~ADD05 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None removed tree and reenergized TREE ON LINE AT BG13AF | ... NO OUTAGE REVIEW INFO
70 | Veg | Durham dlm4375 | ASHE STREET - 14021203 | 7/25/2018 12:03 | 7/25/2018 15:22 | 10841926 | SolidBar - ABC Size: 100 Solid Bar FID: 87234630 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DD Co-dominate stem | 29 Conductor, bare | OB Oak, white | 38 | F2 Forced Outage | 04 Wind, Rain and Lightning | 633 | 2214 | 199 | 620 clayton rd | CMPL 2018-07-25 15:35:00 by JAU4299 RMK: TEER,ERIC IS ALSO ON 131 ON SITE LOCK OUT... FMAG 2066 AB TRIP 50, POSSIBLE FAULT LOCATION NEAR THE INTERSECTION OF CHEEK RD AND JUNCTION RD. 2806 CHEEK RD....live tree across all 3 phases. tree crew removed. dropped circuit to close solid blades at cheek rd. johnnyu.. | dlm4375...thunder storm in area... circuit out see 108421815 ..we had defective at base of tree, co dominate stem tree fall 38' located 800blk of Clayton Rd which is behind a recloser facid 38998786 but the circuit went out because the recloser was bypassed due to a bad modem. Crew opened 300 amp solid blade facid 87234630 see 10841926 to isolate and get circuit back on. After removing tree by tree crew our crew opened circuit again see 1042297 to close in solid blades. fu to GIS to fix annotation on solid blade ticket and also sent inquiry on the modem replacement. ~~~ 7/25/2018 ¦ dlm4375 ¦ Investigative Action
71 | Veg | Durham dlm4375 | FAIRNTOSH - 14142407 | 7/25/2018 12:13 | 7/25/2018 13:50 | 10841835 | S-CKT - ABC Size: Class 3 FID: 38356449 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | NA | OW Oak, willow | 23 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1898 | 1903 | 97 | 1117 milton rd | CMPL 2018-07-25 14:07:00 by RAH6412 RMK: CRKT LOCKOUT - TRIP 51 - AC TARGETS - FMAG 2297 - POSSIBLE FAULT LOCATION INTERSECTION OF GOODWIN RD & N ROXBORO RD | rlw-STORM IN AREA-crew removed live overhanging (23') willow oak limbs from primary in front of 1117 Milton Rd and had the circuit re-energized. Limbs weighted down by the rain. See outage ID# 10841835.Email to veg. to have spot trimmed. ~~~ 7/26/2018 ¦ dlm4375 ¦ Vegetation Management
72 | Veg | Sanford i25781 | SANFORD HORNER BLVD. 230KV - COLONIAL ACRES 23KV | 7/26/2018 06:36 | 7/26/2018 07:16 | 4750799-1 | RECLOSER - YZ FID: 108648_2485045 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | OA Oak | 17 | F2 Forced Outage | 00 Calm | 877 | 2085 | 40 | U189AC | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | JWW// On 7/26/18 at 06:36am a limb fell on primary locking out A and B phase of G&W 108648. When Tech arrived he had DCC drop C phase at 07:00am so he could remove limb off of primary. Once limb was removed tech had DCC energize the G&W at 07:16am restoring power to all 1310 customers. C phase is accounted for in outage 4750807. ~~~ 7/31/2018 ¦ i25781 ¦ Vegetation Management
73 | Veg | Sanford i25781 | SANFORD HORNER BLVD. 230KV - COLONIAL ACRES 23KV | 7/26/2018 07:26 | 7/26/2018 07:39 | 4750813-1 | RECLOSER - BC FID: 108648_2485045 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | OA Oak | 17 | F2 Forced Outage | 00 Calm | 734 | 2085 | 13 | U189AC | Tree/Vegetatn Limb Fell from Outside Right of Way None limb | JWW// On 7/26/18 at 07:26am a limb fell on primary at U189AC locking out B and C phase on G&W 108648 causing 730 customers to loose power. When tech arrived he got limb off with telescopic stick the had DCC energize B and C phase restoring power to all 730 customers. There was another outage (4750799) on this 15 minutes before at the same pole. A work order has been made to cut tree. ~~~ 7/31/2018 ¦ i25781 ¦ Vegetation Management
74 | Veg | Zebulon i70604 | WENDELL 230KV - WENDELL HIGHWAY 64 24KV | 7/28/2018 18:59 | 7/28/2018 19:58 | 4752524-2 | OCB - ABC FID: T5378B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | NA | OA Oak | 21 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1,038 Cust Eq: 1713 | 2791 | 59 | Line~E855BF_E859BF_1728417 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE | CPS// A 65' tall pin oak tree fell from outside of R/W onto conductor near dis#E859BF causing the circuit breaker to open. Self healing team operated correctly restoring 1713 customers (reflected in step 1). Responding line techs removed tree from line and requested DCC close the circuit breaker (reflected in step 2). No damage to equipment. Tree roots were rotten and there was visible stem decay as well. The base of the tree was 21' from centerline. Note the correct recloser dis# for step one is 18CD81 ~~~ 7/30/2018 ¦ i70604 ¦ Investigative Action
75 | Veg | Raleigh e68825 | CHESTNUT HILLS 115KV - NORTH GLEN 23KV | 7/30/2018 03:37 | 7/30/2018 05:34 | 4753845 | RECLOSER - XZ FID: E069BL_104130025 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LR Tree limb, dead, overhang | D2 Dead | NA | PV Pine, Virginia | 5 | F2 Forced Outage | 02 Rain | 1175 | 2553 | 117 | Fuse~E135BL_2876238 | Tree/Vegetatn Limb Fell from Inside Right of Way None limb on at e135bl limb on at e135bl | PEEL 7/31/18: A 1/2" dia. x 3' long dead limb fell from a 2.5' dia. x ~80' tall Virginia Pine, 25' off of line CL, landed on dip dead-end pole E135BL and lodged into the A&C phase cutouts & risers, blew the fuses, and locked out A&C phases of recloser E069BL. No damage. Responding service tech knocked the limb off, & had DCC remotely close the recloser phases back in to restore service. ~~~ 7/31/2018 ¦ e68825 ¦ Investigative Action
76 | Veg | Garner c72037 | WAKE TECH 230KV - BANKS 24KV | 8/1/2018 13:06 | 8/1/2018 18:40 | 4755756 | SECTNLIZER - ABC FID: D301BH_2778766 | 10 Sectionalizer | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DC Internal stem decay | 48 Transformer | OA Oak | 36 | F2 Forced Outage | 00 Calm | 551 | 1808 | 334 | Recloser~D301BH_2778766 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None oak tree on primary | MHS-A live defective oak tree Branch about 36" in DIA. and about 25' from ground level fell 36' from C/L . falling across all 3 phases opening up sectionalizer's at D301BH. Limb busted primary bushing on transformer. crew removed limb off of line and replaced transformer ~~~ 8/7/2018 ¦ c72037 ¦ Investigative Action
77 | Veg | Sanford i25781 | SANFORD HORNER BLVD. 230KV - CHATHAM STREET 23KV | 8/1/2018 16:11 | 8/1/2018 16:39 | 4755815 | RECLOSER - BC FID: R059AC_103526827 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | NA | OA Oak | 7 | F2 Forced Outage | 00 Calm | 793 | 1953 | 28 | J221AC | Tree/Vegetatn Limb Fell from Inside Right of Way None back on | Jeff Ward// On 8/1/18 at 04:11pm a small limb fell from established overhang across B and C phase and locked out G&W R059AC. When Tech arrived he got the limb off with a stick and had DCC energize the G&W at 04:39pm restoring power to all 793 customers. ~~~ 8/9/2018 ¦ i25781 ¦ Investigative Action
78 | Veg | Garner c72037 | WAKE TECH 230KV - TWIN CREEKS 24KV | 8/2/2018 14:55 | 8/2/2018 15:53 | 4756616 | RECLOSER - ABC FID: D860BH_103378776 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | 37 Removed Limb or Tree From Lin | NA | OR Oak, red | 60 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1992 | 2340 | 58 | Recloser~D860BH_103378776 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE @ DIS RG307 TREE @ RG307 | MHS- Crew found a dead Red Oak tree about 30" in DIA. that had fell about 60' from C/L and breaking at ground level across all 3 phases locking out recloser at D860BH. crew cleared tree from line and had DCC reenergize the recloser at D860BH ~~~ 8/15/2018 ¦ c72037 ¦ Investigative Action
79 | Veg | Garner c72037 | FUQUAY 230KV - FUQUAY 23KV | 8/2/2018 15:04 | 8/2/2018 18:17 | 4756660 | FUSE - ABC FID: B398BH_2668786 | 03 Line Fuse | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | 38 Insulator | OB Oak, white | 35 | F2 Forced Outage | 04 Wind, Rain and Lightning | 732 | 2336 | 193 | Fuse~B398BH_2668786 | Tree/Vegetatn Limb Fell from Outside Right of Way None Tree limb broke out and landed in 3 phase line at 15KT86, Wire off insulator on center phase at B404BH. crew to make repairs. Tree limb broke out and landed in 3 phase line at 15KT86, Wire off insulator on center phase at B404BH. crew to make repairs. kv | MHS- Live White Oak Branch about 16" in Dia. broke out of tree 50' above ground level and 35' from C/L falling across all 3 phases at 15KT86 and blowing fuses at B398BH. When limb fell across line it broke insulator on middle phase at B404BH. Crew replaced insulator and cut tree limb off of line ~~~ 8/8/2018 ¦ c72037 ¦ Investigative Action
80 | Veg | Durham AArias | POPE ROAD - 14082403 | 8/3/2018 02:57 | 8/3/2018 04:24 | 108539131 | S-RCL - ABC Size: 800 VPST FID: 38998783 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | PP Pole | OA Oak | 50 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1156 | 3214 | 87 | 3515 Garrett Rd | CMPL 2018-08-03 04:50:00 by VDB7113 RMK: tree down broken pole and wire down. cleared. | aarias// storm in area. ORIGINAL 10853903 TICKET ASSOCIATED TO RCL 392798230. Large oak tree across from 3615 Garrett Rd uprooted and fell on primary from 50 ft away possibly due to lot grading for new construction. Tore all phases of primary from recloser pole, and damaged adjacent pole (tkt 10853903). Damage isolated by cutting jumpers South of Cresset Christian Academy and backfeeding from Pope Rd 2410 by closing N/O RCL 398668029 (tkt 108539031). Blinked upstream recloser, FACID 38998783 (tkt 10853900) before it went out at the same time as RCL 392798230 (tkt 10853913). RCL 38998783 opened to restore feed back to normal after repairs were complete (tkt 10854882). RCL 392798230 remained bypassed for damage inspection until 8/4 ~~~ 8/13/2018 ¦ AArias ¦ Investigative Action
81 | Veg | Durham rlw2159 | DURHAM MAIN - 14011203 | 8/3/2018 07:00 | 8/3/2018 07:23 | 10854111 | S-CKT - ABC Size: Class 2 FID: 38355237 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | 29 Conductor, bare | OA Oak | 11 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1893 | 1894 | 23 | GLENDALE AVE & W MARKHAM AVE TREE ON LINE | locked out with targets 50 a to b and unable to get FMAG due to relay not communicating | rlw2159..storm in area..circuit out see 10854111 due to Defective Oak limb falling on line from approximately 11 at Markham & Acadia. Crew dropped circuit again see 10854252 to fix Burnt Jumper located at Markham Ave and Acadia Ave due to tree on line ~~~ 8/8/2018 ¦ rlw2159 ¦ Investigative Action
82 | Veg | Durham AArias | POPE ROAD - 14082403 | 8/3/2018 11:55 | 8/3/2018 13:05 | 108548821 | S-RCL - ABC Size: 800 VPST FID: 38998783 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DE Erosion/poor enviornment | PP Pole | OA Oak | 50 | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 1082 | 3214 | 70 | aarias// 3615 Garrett Rd | LOCKOUT..TARGETS B TO G..FMAG 2009..UNKNOWN CAUSE..REST..DBH5735 | aarias// storm in area. ORIGINAL 10853903 TICKET ASSOCIATED TO RCL 392798230. Large oak tree across from 3615 Garrett Rd uprooted and fell on primary from 50 ft away possibly due to lot grading for new construction. Tore all phases of primary from recloser pole, and damaged adjacent pole (tkt 10853903). Damage isolated by cutting jumpers South of Cresset Christian Academy and backfeeding from Pope Rd 2410 by closing N/O RCL 398668029 (tkt 108539031). Blinked upstream recloser, FACID 38998783 (tkt 10853900) before it went out at the same time as RCL 392798230 (tkt 10853913). RCL 38998783 opened to restore feed back to normal after repairs were complete (tkt 10854882). RCL 392798230 remained bypassed for damage inspection until 8/4 ~~~ 8/13/2018 ¦ AArias ¦ Investigative Action
83 | Veg | Cary JOCHRIS | GREEN LEVEL 115KV - WILSONVILLE 24KV | 8/4/2018 01:48 | 8/4/2018 02:31 | 4758240 | RECLOSER - XYZ FID: CCY03_2585265 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin | 29 Conductor, bare | OR Oak, red | 51 | F2 Forced Outage | 02 Rain | 1015 | 1403 | 43 | Line~6AF46_275K_2550087 | Tree/Vegetatn Limb Fell from Inside Right of Way None Tree limb fell and brushed 2 phases of primary on the way down opening recloser CCY03. Bryan M. | O. Christian - 8/10/2018 - 24" diameter red oak tree limb broke away from 60" diameter tree trunk 25' above ground at 51' from CL contacting line and locking out recloser CCY03. No damage to conductors, poles or line hardware. Limb removed from line and service restored. ~~~ 8/10/2018 ¦ JOCHRIS ¦ Investigative Action
84 | Veg | Roxboro i67431 | ROXBORO SOUTH 230KV - BUSHY FORK 23KV | 8/4/2018 01:53 | 8/4/2018 02:45 | 4758252-2 | SWITCH - ABC FID: EZ578_110932318 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 18 | F2 Forced Outage | 00 Calm | 844 | 2516 | 52 | Line~E1C69_E1C70_2558828 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree on primary tree on primary | DPW: Dead Pine tree fell across primary at E1C72-E1C73 locking out AB phase of recloser 9T915. Switch EZ578 was opened to sectionalize customers. Limb was removed and feed put back to normal. A mid span fault was located and an order is to be written to correct the mid span fault area by changing to crossarm construction. ~~~ 8/8/2018 ¦ i67431 ¦ Investigative Action
85 | Veg | Roxboro i67431 | ROXBORO SOUTH 230KV - BUSHY FORK 23KV | 8/4/2018 01:53 | 8/4/2018 02:30 | 4758252-1 | RECLOSER - AB FID: 9T915_110989237 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | 20 Cut In/Reconnect at Pole | NA | PT PINE | 18 | F2 Forced Outage | 00 Calm | 774 | 2516 | 37 | Line~E1C69_E1C70_2558828 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree on primary tree on primary | DPW: Dead Pine tree fell across primary at E1C72-E1C73 locking out AB phase of recloser 9T915. Switch EZ578 was opened to sectionalize customers. Limb was removed and feed put back to normal. A mid span fault was located and an order is to be written to correct the mid span fault area by changing to crossarm construction. ~~~ 8/8/2018 ¦ i67431 ¦ Work Order(s) Generated
86 | Veg | Cary JOCHRIS | RALEIGH OAKDALE 230KV - ROYLENE 23KV | 8/4/2018 13:56 | 8/4/2018 14:56 | 4758543-1 | SWITCH - ABC FID: H412K_2771859 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | 37 Removed Limb or Tree From Lin | 29 Conductor, bare | PW Pine, white | 24 | F2 Forced Outage | 00 Calm | 2359 | 2804 | 60 | Line~GP21K_GP20K_2767088 | Tree/Vegetatn Limb Fell from Inside Right of Way None Tree from outside ROW fell on doeble circuit. Bryan M. Tree from outside ROW fell on doeble circuit. Bryan M. | O. Christian - 10/3/2018 - 8" diameter dead white pine tree 24' from CL fell onto double circuit at GP20K taking out the breaker on the Farmgate 23KV FDR and switch H412K on the Roylene 23KV FDR. Tree removed from line and service restored. ~~~ 10/3/2018 (60 days) ¦ JOCHRIS ¦ Investigative Action
87 | Veg | Cary JOCHRIS | RALEIGH OAKDALE 230KV - FARM GATE 23KV | 8/4/2018 13:56 | 8/4/2018 15:07 | 4758551-1 | OCB - ABC FID: T5136B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | 37 Removed Limb or Tree From Lin | 29 Conductor, bare | PW Pine, white | 24 | F2 Forced Outage | 00 Calm | 1068 | 2292 | 71 | Node~GP24K_2745354 | Tree/Vegetatn Limb Fell from Inside Right of Way None Tree from outside ROW fell on doeble circuit. Bryan M. Tree from outside ROW fell on doeble circuit. Bryan M. | O. Christian - 10/3/2018 - 8" diameter dead white pine tree 24' from CL fell onto double circuit at GP20K taking out the breaker on the Farmgate 23KV FDR and switch H412K on the Roylene 23KV FDR. Tree removed from line and service restored. ~~~ 10/3/2018 (60 days) ¦ JOCHRIS ¦ Investigative Action
88 | Veg | Cary c72037 | FUQUAY BELLS LAKE 230KV - OPTIMIST FARM 23KV | 8/5/2018 21:13 | 8/5/2018 22:00 | 4759431-1 | OCB - ABC FID: T4866B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | DC Internal stem decay | NA | OR Oak, red | 25 | F2 Forced Outage | 00 Calm | 1850 | 1866 | 47 | Line~7790K_7791K_2728171 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | MHS-Crew rode line out and found a dead Red Oak limb About 6" in DIA. had broke off about 35' Above ground level and 25' form C/L. when it fell across all 3 phases it locked out the FCB. Crew removed the limb and had DCC re-energize the FCB ~~~ 8/15/2018 ¦ c72037 ¦ Investigative Action
89 | Veg | Henderson i67431 | YOUNGSVILLE 115KV - HARRIS CROSSROADS 24KV | 8/6/2018 14:15 | 8/6/2018 15:20 | 4759931-1 | RECLOSER - BC FID: EKC14_1672042 | 02 Line Recloser | OH Distribution Line Overhead |  | LX Trees, overgrown primary | DN No apparent defect | 29 Conductor, bare | UU Unknown Manufacturer | 0 | F2 Forced Outage | 00 Calm | 1186 | 2408 | 65 | Line~EH534_EH535_1637730 |  | DPW: At EH532 to EH535, tree growth pushed the neutral into primary locking out BC phases. Note: the customer had been hearing 'buzzing' in the line the day before. Service tech stated that permission was given to close recloser back in with BC phases still locked out. Crew repaired burned down neutral. (incomplete at this time) ~~~ 8/8/2018 ¦ i67431 ¦ Investigative Action
90 | Veg | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 8/7/2018 04:38 | 8/7/2018 06:20 | 4775937-1 | OCB - ABC FID: T4720B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | 39 Repaired Overhead Conductor | 29 Conductor, bare | OR Oak, red | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1357 | 2736 | 102 | T753BJ | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Tree on 477 at T753BJ. | MHS- Crew found a Dead Red Oak tree about 16" in DIA. had fallen across all 3 phases tearing down a phase at T753BJ. The tree broke about 5' above ground level and 42' from C/L. crew than opened up G&W BR21BJ and had DCC hot the FCB back up getting back 1357 customers on. crew than went to Air Break switch T490BJ and opened it up and had DCC close in G&W BR21BJ which got 875 customers on the remaining 494 customers stayed off till repairs were done ~~~ 8/15/2018 ¦ c72037 ¦ Investigative Action
91 | Veg | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 8/7/2018 04:38 | 8/7/2018 06:35 | 4775937-2 | RECLOSER - ABC FID: BR21BJ_104162335 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | 39 Repaired Overhead Conductor | 29 Conductor, bare | OR Oak, red | 42 | F2 Forced Outage | 04 Wind, Rain and Lightning | 875 | 2736 | 117 | T753BJ | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Tree on 477 at T753BJ. | MHS- Crew found a Dead Red Oak tree about 16" in DIA. had fallen across all 3 phases tearing down a phase at T753BJ. The tree broke about 5' above ground level and 42' from C/L. crew than opened up G&W BR21BJ and had DCC hot the FCB back up getting back 1357 customers on. crew than went to Air Break switch T490BJ and opened it up and had DCC close in G&W BR21BJ which got 875 customers on the remaining 494 customers stayed off till repairs were done ~~~ 8/15/2018 ¦ c72037 ¦ Investigative Action
92 | Veg - MED | Durham rlw2159 | GREEN STREET - 14121202 | 8/8/2018 16:16 | 8/8/2018 23:10 | 10862691 | FOH - ABC Size: 175 SMU-20 (E) FID: 38841183 | 03 Line Fuse | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DC Internal stem decay | 29 Conductor, bare | OW Oak, willow | 17 | F2 Forced Outage | 04 Wind, Rain and Lightning | 532 | 1210 | 414 | 2300 CHAPEL HILL RD | CMPL 2018-08-08 23:10:00 by NZJACKS RMK: Tree @ chapel hill and Vesson Rd, Broken neutral and x-arm. Open 175E @ Merrimac and Morehead /// Cleared tree, repaired arm, refused 175E. | RLW-STORM IN AREA--APPROXIMATELY A 14" AROUND DEFECTIVE WILLOW OAK BRANCH FELL BREAKING ARMS AND TEARING DOWN 2 PHASES OF PRIMARY.CREW CHANGED ARMS AND PUT PRIMARY UP THEN REFUSED 175 E FUSES. TREE CREW WAS CALLED FOR AT 1840. RELATED TO 10863883 ~~~ 8/10/2018 ¦ rlw2159 ¦ Investigative Action
93 | Veg - MED | Chatham County JOCHRIS | BYNUM 230KV - BYNUM 23KV | 8/8/2018 18:00 | 8/8/2018 19:06 | 4763072-2 | OCB - ABC FID: T1025B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | SZ Sweet Gum | 2 | F2 Forced Outage | 04 Wind, Rain and Lightning | 3727 | 4107 | 66 | Line~AU74AF_13T713_2464513 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE FELL ACROSS ALL 3 PHASES AT AU74AF Tree @ AU74AF across 3 phases | O. Christian - 10/8/2018 - 10" diameter sweet gum tree 2' off CL fell over 1' above ground level due to beavers eating out the tree at its base, falling on line causing FCB to open. Tree removed and recloser closed and service returned. ~~~ 10/8/2018 (61 days) ¦ JOCHRIS ¦ Investigative Action
94 | Veg - MED | Chatham County JOCHRIS | BYNUM 230KV - JACK BENNETT 23KV | 8/8/2018 18:06 | 8/8/2018 19:40 | 4763163 | RECLOSER - ABC FID: 1D3N05_115038488 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | MR Maple, red | 33 | F2 Forced Outage | 04 Wind, Rain and Lightning | 766 | 1899 | 94 | Fuse~8XP67_115150506 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | O. Christian - 10/3/2018 - 10" diameter maple tree limb 33' off the CL broke off tree trunk 28' above the ground contacting the vertical 3 phase construction 32' from pole 8XP67 causing recloser 1D3N05 to open. Tree limb removed and service restored. ~~~ 10/3/2018 (56 days) ¦ JOCHRIS ¦ Investigative Action
95 | Veg - MED | Asheboro i25781 | RAMSEUR 115KV - FRANKLINVILLE 24KV | 8/8/2018 18:21 | 8/8/2018 18:55 | 4763145-2 | OCB - ABC FID: T1390B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | OA Oak | 23 | F2 Forced Outage | 04 Wind, Rain and Lightning | 919 Cust Eq: 1066 | 1996 | 34 | 0181AD | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None LIMB ON ALL 3 PHASES AT 0181AD | JWW// On 8/8/18 at 6:21pm during a strong thunderstorm a tree limb fell from outside of right of way at 0181AD across all 3 phases locking out the Franklinville FDR. This FDR has 1985 customers on it. The self healing G&W at 98G01 closed in picking up 1066 customers leaving only 919 customers without power. When tech arrived he removed the limb with a telescopic stick then had DCC energize the FDR at 6:55pm, this restored power to the remaining 919 customers. ~~~ 8/16/2018 ¦ i25781 ¦ Investigative Action
96 | Veg - MED | Raleigh DFontan | RALEIGH YONKERS ROAD 115KV - SUNNYBROOK ROAD 24KV | 8/8/2018 18:56 | 8/8/2018 20:48 | 4763255 | OCB - ABC FID: T5126B11 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | AS Ash | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1337 | 1343 | 112 | C122BJ - C123BJ | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE C122BJ - C123BJ | Fontana 8/9/18, Peel 8/22/18 - An 8" x ~30' long live limb of an American Mountain Ash 15' from the line CL overhanging the line broke ~5' from the line CL , laid across the feeder primaries in span C122BJ - C123BJ, and locked out the FCB. Responding C&M Tech cleared the limb from the line and had DCC remotely close the FCB to restore service. ~~~ 8/9/2018 ¦ DFontan ¦ Investigative Action
97 | Veg - MED | Chatham County JOCHRIS | PITTSBORO 230KV - BIG WOODS 23KV | 8/8/2018 19:14 | 8/8/2018 20:22 | 4763321 | RECLOSER - XYZ FID: CS64AF_2577172 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin | NA | OR Oak, red | 32 | F2 Forced Outage | 04 Wind, Rain and Lightning | 764 | 1427 | 68 |  | Tree/Vegetatn Tree/Limb Growth None Tree limb across 3 phases @ CZ70AF Tree limb across 3 phases @ CZ70AF | O. Christian - 10/8/2018 - 10" diameter live red oak tree limb from 36" diameter tree 32' off CL fell contacting line and knocking out recloser CS64AF and taking out 764 customers. Limb removed from line and service restored. ~~~ 10/8/2018 (61 days) ¦ JOCHRIS ¦ Investigative Action
98 | Veg - MED | Selma i70604 | FOUR OAKS 230KV - HANNAHS CREEK 24KV | 8/8/2018 19:52 | 8/8/2018 23:53 | 4763146 | RECLOSER - ABC FID: V901_104479318 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | LL Tree limb fails | DN No apparent defect | NA | PT PINE |  | F2 Forced Outage | 11 Tornado/Wind Shear/Microburst | 925 | 1553 | 241 | VD77BA | Overhead Fac Overhead Secondary / Service Failure Conductor Broke/Burned Down sec burned up bad sec trees rubbed wire into | CPS// Crew remarks for this outage are incorrect (not related to this outage)// A severe thunderstorm with 60MPH winds caused a 44" live pine limb to break out and fall on the conductor near dis#VD77BA. This event opened G&W V901. Limb was removed and the line was re-energized// No damage to equipment // Could not determine the exact location on the tree where the live limb broke from. ~~~ 8/10/2018 ¦ i70604 ¦ Investigative Action
99 | Veg - MED | Zebulon i70604 | NASHVILLE 115KV - WEST NASH 23KV | 8/8/2018 21:13 | 8/8/2018 21:25 | 4763683 | OCB - ABC FID: T5900B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | CH Black Cherry (Wild) | 52 | F2 Forced Outage | 04 Wind, Rain and Lightning | 2170 | 2190 | 12 | 444BC | Tree/Vegetatn Limb Fell from Inside Right of Way None TREE ACROSS ALL 3 PHASES AT 444BC TREE ACROSS ALL 3 PHASES AT 444BC | CPS// A 75' tall dead Black Cherry tree fell near dis#444BC contacting both the West Nash and the Nashville feeders causing both breakers to open// Base of the tree was 52' from center line up on an embankment// No damage to our facilities// Responding line tech was able to remove the tree and restore both circuits// Associated outage is #4763684 ~~~ 8/9/2018 ¦ i70604 ¦ Investigative Action
100 | Veg - MED | Zebulon i70604 | NASHVILLE 115KV - NASHVILLE 23KV | 8/8/2018 21:14 | 8/8/2018 21:26 | 4763684 | OCB - ABC FID: T5900B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | CH Black Cherry (Wild) | 52 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1612 | 1608 | 12 | 444BC | Tree/Vegetatn Limb Fell from Inside Right of Way None TREE LIMB FELL ACROSS AT 444BC TREE LIMB FELL ACROSS AT 444BC | CPS// A 75' tall dead Black Cherry tree fell near dis#444BC contacting both the West Nash and the Nashville feeders causing both breakers to open// Base of the tree was 52' from center line up on an embankment// No damage to our facilities// Responding line tech was able to remove the tree and restore both circuits// Associated outage is #4763683 ~~~ 8/9/2018 ¦ i70604 ¦ Investigative Action
101 | Veg | Selma i70604 | FOUR OAKS 230KV - HANNAHS CREEK 24KV | 8/9/2018 00:10 | 8/9/2018 00:36 | 4763887-1 | RECLOSER - ABC FID: V901_104479318 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | 29 Conductor, bare | CY Cypress, Leyland | 16 | P4 Crew Initiated Outage | 11 Tornado/Wind Shear/Microburst | 889 | 1553 | 26 | VD19BA | Tree/Vegetatn Tree/Limb Growth None TREE LIMB @ VD10BA | CPS// During a severe thunderstorm a Leland Cypress tree was blown over onto pole dis#VD19BA. The tree was 16' from center line. Responding Line & Service techs request DCC to open G&W V901 so the tree could be cleared. Lightning arresters, Cutouts, and the main line neutral were damaged. ~~~ 8/10/2018 ¦ i70604 ¦ Investigative Action
102 | Veg | Chatham County JOCHRIS | PITTSBORO 230KV - PITTSBORO 23KV | 8/10/2018 11:39 | 8/10/2018 12:28 | 4765161 | OCB - ABC FID: T2250B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | 37 Removed Limb or Tree From Lin | 36 Cutout, fused | OB Oak, white | 41 | F2 Forced Outage | 00 Calm | 2140 | 2163 | 49 | Load~AM93AF | Tree/Vegetatn Tree/Limb Growth None TREE FELL BUSTING CUTOUT | O. Christian - 8/23/2018 - 18' diameter live white oak tree 41' off CL broke off and fell into line breaking cutout and locking out FCB. Tree removed and service restored. ~~~ 8/23/2018 ¦ JOCHRIS ¦ Investigative Action
103 | Veg | Raleigh e68825 | LAKESTONE 115KV - CURRITUCK 12KV | 8/11/2018 20:07 | 8/11/2018 21:09 | 4766173 | RECLOSER - BC FID: J063BL_104494240 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 28 Patrolled & No Problem Found | NA | UN Unknown Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 534 | 1297 | 62 | J113BL-J117BL | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None Trees blew into power lines during strong thunderstorm. Reclosure outgage from trees inside right of way. | PEEL 8/21/18: During strong thunderstorm, G#W recloser J063BL locked out due to a B-C phase-to-phase fault. Responding C&M tech patrolled the feeder beyond the recloser, saw numerous trees close to the line, but found all were in the clear. They could not determine which tree caused the fault. They had DCC close in the recloser to restore service. Engineers performed an FMS/Cyme fault analysis, and found the possible fault location to be along Northbrook Drive btwn. J113BL & J117BL. We patrolled the feeder from the recloser J063BL out to the end of Northbrook Drive (J117BL), but could not ascertain which tree had actually caused the fault. ~~~ 8/21/2018 ¦ e68825 ¦ Investigative Action
104 | Veg | Raleigh DFontan | LAKESTONE 115KV - CURRITUCK 12KV | 8/12/2018 09:23 | 8/12/2018 10:03 | 4766735 | RECLOSER - BC FID: J063BL_104494240 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect |  | 28 Other Species | 0 | F2 Forced Outage | 00 Calm | 537 | 1297 | 40 | Fuse~J102BL_2868287 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ACROSS ALL THREE PHASES INSIDE RIGHT OF WAY | Fontana 8/14/18 - Spoke to customers who said they saw sparks flying from where a crepe myrtle had grown into the lines. They claim they flagged down a Duke service crew who trimmed the Crepe Mrytle. There were no visible burn marks or signs of damage to Duke equipment. ~~~ 8/14/2018 ¦ DFontan ¦ Investigative Action
105 | Veg | Asheboro i25781 | TROY BURNETTE STREET 115KV - ELDORADO 13kV | 8/12/2018 16:55 | 8/12/2018 18:47 | 4766998-1 | OCB - ABC FID: T1612B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 23 | F2 Forced Outage | 04 Wind, Rain and Lightning | 739 | 731 | 112 | Line~1266_1267_2239016 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | JWW// On 8/12/18 at 04:55pm during a strong thunderstorm a small dead pine tree fell from outside of the right of way across all 3 phases locking out the Eldorado FDR. When the Tech arrived he cut the dead pine tree off of the primary and had DCC energize the FDR at 06:47pm restoring power to 739 customers. ~~~ 8/13/2018 ¦ i25781 ¦ Investigative Action
106 | Veg | Zebulon i70604 | ROCKY MOUNT 230KV - EASONBURG 23KV | 8/12/2018 19:23 | 8/12/2018 19:56 | 4767088-1 | RECLOSER - ABC FID: 9TX93_110657240 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | NA | MM Mimosa | 37 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1884 | 1916 | 33 | BY48BC | Tree/Vegetatn Limb Fell from Outside Right of Way None | CPS// 65' hard wood with defective roots and visible stem decay fell from outside of R/W contacting conductor at BY48BC causing circuit breaker to open. The responding service tech opened air break switch BY53BC to isolate fault. DCC dispatch then closed G&W 9TX93 (Reflected in step 1). Line techs removed the tree from the conductor and re-energized the circuit breaker restoring all remaining customers (Reflected in step 2). No damage to equipment. Tree was 37' from center line. ~~~ 8/14/2018 ¦ i70604 ¦ Investigative Action
107 | Veg | Henderson i67431 | OXFORD NORTH 230KV - OXFORD EAST 23KV | 8/13/2018 03:10 | 8/13/2018 04:54 | 4767560-5 | SWITCH - ABC FID: ETU32_109182338 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 18 | F2 Forced Outage | 04 Wind, Rain and Lightning | 502 | 1019 | 104 | Load~ETV33 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree on line at etv33 tree on line at etv33 | DPW: On 8/13/18, the Oxford East Feeder locked out due to a tree on the line at DIS # ETV33. This impacted 1015 ***DUPLICATE ORDER*** customers off for 104 minutes. Distribution switching is as follows: SHNT restored 423 customers after 2 minutes, 209 customers off for 53 minutes, and 383 customers off for 104 minutes. Total CMI - 51755 ~~~ 8/13/2018 ¦ i67431 ¦ Investigative Action
108 | Veg | Henderson i67431 | HENDERSON NORTH 115KV - WILLIAMSBORO 23KV | 8/14/2018 01:27 | 8/14/2018 02:50 | 4768412 | RECLOSER - ABC FID: 17EN01_104125427 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | OA Oak | 20 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1158 | 2497 | 83 | Line~ENB47_ENB48_1648833 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell at pole ENB48 tore down neutral in 2 spans | DPW: Dead Oak tree fell at ENB48 and brought down the neutral in two spans. Neutral was repaired/installed back onto section of feeder. ~~~ 8/14/2018 ¦ i67431 ¦ Investigative Action
109 | Veg | Garner c72037 | FUQUAY 230KV - FUQUAY 23KV | 8/17/2018 21:02 | 8/17/2018 21:09 | 4772342 | OCB - ABC FID: T4710B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin | NA | SZ Sweet Gum | 18 | F2 Forced Outage | 00 Calm | 3292 | 2336 | 7 | F306BH | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE AT F306BH | MHS- crew found a live Sweet Gum tree branch about 7" in DIA. that had broke out of the tree about 60' from ground level and 18' from C/L. It fell across all 3 phases locking out the FCB. Crews removed the limb and DCC hot the feeder back up. ~~~ 8/28/2018 ¦ c72037 ¦ Investigative Action
110 | Veg | Garner c72037 | GARNER 115KV - VANDORA SPRINGS 24KV | 8/18/2018 21:41 | 8/18/2018 22:44 | 4774053 | RECLOSER - AB FID: 146W86_113087425 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | 26 Vines | 27 Other/See Notes | A1 Arrester, polymer | UN Unknown Species |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1763 | 2281 | 63 | 105T21 | Tree/Vegetatn Tree/Limb Growth None VINES WRAPPED AROUND POLE AT 105T21 VINES WRAPPED AROUND POLE AT 105T21 | MHS- Crew rode line out finding vines wrapped around pole 105T21 having blown lighting arrestor but not clearing which in turn opened up recloser at 146W86. Crew cut vines from pole and cleared arrestor. then had DCC re-energize recloser 146W86. did W/O 29676533 to replace arrestors ~~~ 8/28/2018 ¦ c72037 ¦ Work Order(s) Generated
111 | Veg | Asheboro i25781 | BISCOE 115KV - STAR NORTH 23KV | 8/18/2018 22:44 | 8/18/2018 23:30 | 4774121 | OCB - ABC FID: T0990B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 16 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1012 | 1011 | 46 | 7405 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree on primary tree on primary | JWW// On 8/18/18 at 10:44pm during a strong thunderstorm a dead pine tree fell from outside the right of way at 7405 locking out the Star North FDR causing 1012 customers to loose power. When the Tech arrived he cut the dead pine tree off of the 3 phase and had DCC energize the FDR at 11:30pm restoring power to all 1012 customers. ~~~ 8/20/2018 ¦ i25781 ¦ Investigative Action
112 | Veg | Henderson i67431 | WARRENTON 115KV - HIGHWAY 401 NORTH 23KV | 8/20/2018 23:00 | 8/20/2018 23:39 | 4776276-1 | SWITCH - ABC FID: EAY50_1860588 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DA Damaged |  | HW HARDWOOD | 24 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1619 | 1697 | 39 | EPB27_EPB28 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | DPW: Live hardwood tree cut by beavers fell on feeder at EPB27-EPB28 locking out the Hwy 401 feeder. Back fed with the Warrenton Feeder. Beavers and beaver dam have been cleared. Will install disconnects to be able to sectionalize. ~~~ 8/29/2018 ¦ i67431 ¦ Investigative Action
113 | Veg | Zebulon i70604 | ROLESVILLE 230KV - MITCHELL MILL 24KV | 8/29/2018 13:18 | 8/29/2018 14:05 | 4783255 | OCB - ABC FID: T5205B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 33 | F2 Forced Outage | 00 Calm | 1,044 Cust Eq: 919 | 1958 | 47 | Line~B423BF_B422BF_1630840 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None small pine tree fell on lines at B423BF small pine tree fell on lines at B423BF | CPS// Dead pine tree 33' from center line fell onto conductor at dis#B423BF causing circuit breaker to open// Self healing team operated correctly and restored 919 customers up to 1AXT88 // Responding line tech removed tree from conductor and DCC closed the circuit breaker// No damage to equipment ~~~ 8/30/2018 ¦ i70604 ¦ Investigative Action
114 | Veg | Henderson i67431 | FRANKLINTON 115KV - COLLEGE STREET 24KV | 9/1/2018 15:35 | 9/1/2018 16:20 | 4786226 | OCB - ABC FID: T4700B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect |  | HW HARDWOOD |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1260 | 1265 | 45 | EP835 | Tree/Vegetatn Limb Fell from Inside Right of Way None | DPW: The College Street Feeder locked out due to a limb on the line. This impacted 1,260...investigation in progress. A small hardwood limb fell across the feeder locking out the College St Feeder. c Customers off for 45 minutes. Total CMI - 56,700 customers off for 45 minutes. Total CMI - 56,700 ~~~ 9/3/2018 ¦ i67431 ¦ Investigative Action
115 | Veg | Raleigh DFontan | MORDECAI 115KV - BLOUNT STREET 12KV | 9/1/2018 16:16 | 9/1/2018 17:47 | 4786257 | OCB - ABC FID: T5005B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LL Tree limb fails | DN No apparent defect | NA | OW Oak, willow | 40 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1098 | 1096 | 91 | G604BK | Overhead Fac Undetermined Feeder Circuit Breaker Lockout STORM likely fault location G850BK, G628BK, G748BK, less likely fault @ HZ95BK | Fontana 9/4/18 - C&M worker patrolled entire line and could not identify the cause of the fault. After performing a CYME analysis we found a small branch lying in the street near pole G604BK. Shortly after a customer came out of his house to tell us he saw the line arcing right where we were looking. We concluded that the branch fell from a 70' tall by 4' diameter Willow Oak tree located about 40 feet off the feeder center line. The small branch laid across A & B phases locking out the FCB ~~~ 9/4/2018 ¦ DFontan ¦ Investigative Action
116 | Veg | Cary JOCHRIS | CARY PINEY PLAINS 230KV - TOWNE CENTER 24KV | 9/1/2018 16:57 | 9/1/2018 18:16 | 4786281 | OCB - ABC FID: T5111B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin | NA |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 578 | 586 | 79 | Switch~T5111B02 | Tree/Vegetatn Tree/Limb Growth None vacuum switch had twig, burnt vicinity DIS N441K, sparking transformer | O. Christian - 9/27/2018 - At N427K very small maple tree branch (twig) fell on top of field side oil switch causing riser to burn off and causing hole to be burned into top of switch causing feeder outage per Line Tech. Work order 29988192 written to replace oil switches with 100E power fuses. Small branch not located. ~~~ 9/27/2018 (26 days) ¦ JOCHRIS ¦ Investigative Action
117 | Veg | Henderson i67431 | OXFORD NORTH 230KV - BEREA 23KV | 9/3/2018 14:27 | 9/3/2018 20:05 | 4787613-7 | RECLOSER - ABC FID: 126M04_2889938 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead |  | OA Oak | 20 | F2 Forced Outage | 00 Calm | 768 | 1947 | 338 | ESJ99_ESJ97 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree has fallen through feeder | DPW: Dead Oak tree fell between ESJ99-ESJ97, locking out the Berea Feeder. ESG80 was closed in to back feed with the Stovall Fdr, EQT81 was closed in to back feed with the Stem Feeder.ESJ47 was opened and 126M04 was opened to isolate the fault location. Tree removed and conductor was repaired, feed put back to normal. Berea Feeder locked out due to a tree falling through the feeder. This impacted 1,937 customers. Distribution switching is as follows: 612 customers off for 46 minutes, 2 customers off for 50 minutes, 272 customers off for 68 minutes, 250 customers off for 92 minutes, 1 customer off for 109 minutes, 32 customers off for 325 minutes, and 768 customers off for 338 minutes. Total CMI - 340,905 ~~~ 9/4/2018 ¦ i67431 ¦ Investigative Action
118 | Veg | Henderson i67431 | OXFORD NORTH 230KV - BEREA 23KV | 9/3/2018 14:27 | 9/3/2018 15:13 | 4787613-1 | OCB - ABC FID: T5090B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead |  | OA Oak | 20 | F2 Forced Outage | 00 Calm | 612 | 1947 | 46 | ESJ99_ESJ97 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree has fallen through feeder | DPW: Dead Oak tree fell between ESJ99-ESJ97, locking out the Berea Feeder. ESG80 was closed in to back feed with the Stovall Fdr, EQT81 was closed in to back feed with the Stem Feeder.ESJ47 was opened and 126M04 was opened to isolate the fault location. Tree removed and conductor was repaired, feed put back to normal. Berea Feeder locked out due to a tree falling through the feeder. This impacted 1,937 customers. Distribution switching is as follows: 612 customers off for 46 minutes, 2 customers off for 50 minutes, 272 customers off for 68 minutes, 250 customers off for 92 minutes, 1 customer off for 109 minutes, 32 customers off for 325 minutes, and 768 customers off for 338 minutes. Total CMI - 340,905 ~~~ 9/4/2018 ¦ i67431 ¦ Investigative Action
119 | Veg | Raleigh e68825 | CHESTNUT HILLS 115KV - NORTH GLEN 23KV | 9/7/2018 11:21 | 9/7/2018 11:56 | 4791022 | RECLOSER - A C FID: E069BL_104130025 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PV Pine, Virginia | 26 | F2 Forced Outage | 00 Calm | 1176 | 2553 | 35 | GP20BL-GP21B | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | PEEL 9/11/18: A 6" dia. x ~50' tall dead Virginia Pine broke off 2' above the GL, fell onto the feeder in span GP20BL-GP21B, laid onto phase conductors A & C, and locked out A & C phases of G&W recloser E069BL. Responding crew had DCC remotely open B phase of the recloser (Outage 4791033) to enable them to safely remove the tree from the line, then had DCC remotely close in the recloser to restore service. ~~~ 9/11/2018 ¦ e68825 ¦ Investigative Action
120 | Veg | Raleigh e68825 | CHESTNUT HILLS 115KV - NORTH GLEN 23KV | 9/7/2018 11:42 | 9/7/2018 11:56 | 4791033 | RECLOSER - B FID: E069BL_104130025 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PV Pine, Virginia | 26 | P4 Crew Initiated Outage | 00 Calm | 723 | 2553 | 14 | GP20BL-GP21B | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | PEEL 9/11/18: A 6" dia. x ~50' tall dead Virginia Pine broke off 2' above the GL, fell onto the feeder in span GP20BL-GP21B, laid onto phase conductors A & C, and locked out A & C phases of G&W recloser E069BL (Outage 4791022). Responding crew had DCC remotely open B phase of the recloser to enable them to safely remove the tree from the line, then had DCC remotely close in the recloser to restore service (Crew-initiated outage). ~~~ 9/11/2018 ¦ e68825 ¦ Investigative Action
121 | Veg | Chapel Hill AArias | HILLSBOROUGH - 19081202 | 9/10/2018 12:36 | 9/10/2018 13:17 | 10896316 | S-CKT - ABC Size: Class 1 FID: 38359317 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | 29 Conductor, bare | AS Ash | 0 | F2 Forced Outage | 00 Calm | 1318 | 1457 | 41 | TREE DAMAGE @ 240 ST MARYS ROAD NEAR TRYON | LINE DOWN/TREE LIMB DAMAGE @ 240 ST MARYS ROAD NEAR TRYON. OPENED SOLID BLADE:39063670 TO ISOLATE FROM BREAKER LOCK OUT. TL526/LUKE MCKINNEY. INSIDE ROW | aarias// live overhang white ash limb fell on primary and took out field and middle phase of primary. Additional dead limb across phases on next span. Opened SBs to isolate damage (tkt 10896391) and FCB opened again to close the SBs once repairs were made (tkt 10896858). Primary wire spliced back up and dead limb removed from adjacent span. FUN to change wire adjacent span from FACID 38590068 to FACID 38590064 due to splices on line <1' away from pole ~~~ 9/11/2018 ¦ AArias ¦ Work Order(s) Generated
122 | Veg | Cary JOCHRIS | RALEIGH SOUTH 115KV - AVENT FERRY 23KV | 9/11/2018 17:21 | 9/11/2018 18:12 | 4796725 | RECLOSER - BC FID: RBH78_104321288 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | 37 Removed Limb or Tree From Lin | 29 Conductor, bare | PW Pine, white | 18 | F2 Forced Outage | 04 Wind, Rain and Lightning | 582 | 1855 | 51 | Load~RBZ46 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | O. Christian - 10/9/2018 - 6" diameter dead white pine tree broke off 3' above the ground 18' off CL fell contacting line and causing outage of recloser RBH78 and 582 customers. Tree removed and service restored. No damage to conductors, line hardware or poles. ~~~ 10/9/2018 (28 days) ¦ JOCHRIS ¦ Investigative Action
123 | Veg - MED | Garner c72037 | ANGIER 230KV - CHALYBEATE 23KV | 9/13/2018 16:23 | 9/13/2018 16:54 | 4799002 | OCB - ABC FID: T5427B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | SZ Sweet Gum | 15 | F2 Forced Outage | 12 Hurricane | 1,949 Cust Eq: 1207 | 1930 | 31 | 2JG08 | Tree/Vegetatn Limb Fell from Inside Right of Way None | MHS- According to service tech small sweet gum branch broke out of tree and fell across all 3 phases locking out FCB. Tech removed limb and had DCC re-energize the FCB. rode out area and could not locate limb. ~~~ 9/26/2018 ¦ c72037 ¦ Investigative Action
124 | Veg - MED | Cary c72037 | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 9/13/2018 23:41 | 9/14/2018 00:49 | 4818785 | OCB - ABC FID: T4866B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE |  | F2 Forced Outage | 12 Hurricane | 2798 | 2825 | 68 | B962BH | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE B962BH | MHS- Walked this whole area out could not find tree limb any where. this is a golf course and they have cleaned everything thing up from the storm. Spoke to line tech. he said that it was a dead pine limb about 3" in DIA., Could not tell where it fell from. ~~~ 10/4/2018 (20 days) ¦ c72037 ¦ Investigative Action
125 | Veg - MED35 | Selma omshistproc | PRINCETON 115KV - PRINCETON 24KV | 9/14/2018 00:22 | 9/15/2018 20:04 | 4819831-2 | RECLOSER - ABC FID: SQ10BA_104317094 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 02 Rain | 899 | 1731 | 2623 | Node~1331111 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Cleared up restored power q667 switch open, dis q679, ptp, top tie, 4462us 70 a princeton | ... NO OUTAGE REVIEW INFO
126 | Veg - MED35 | Selma omshistproc | PRINCETON 115KV - PRINCETON 24KV | 9/14/2018 00:22 | 9/15/2018 20:00 | 4819831-1 | JUMPER - ABC FID: JUMPER-611078 | 09 Jumper/wire cut/open | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 02 Rain | 791 | 1731 | 2619 | Node~1331111 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Cleared up restored power q667 switch open, dis q679, ptp, top tie, 4462us 70 a princeton | ... NO OUTAGE REVIEW INFO
127 | Veg - MED35 | Selma omshistproc | SELMA 230KV - BROGDEN 23KV | 9/14/2018 01:00 | 9/15/2018 18:00 | 4831332 | RECLOSER - ABC FID: RF37BA_104153731 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 584 | 1823 | 2460 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None trees trees | ... NO OUTAGE REVIEW INFO
128 | Veg - MED35 | Cary JOCHRIS | GREEN LEVEL 115KV - WILSONVILLE 24KV | 9/14/2018 01:09 | 9/15/2018 09:27 | 4823260 | OCB - ABC FID: T4603B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | SZ Sweet Gum | 18 | F2 Forced Outage | 03 Wind | 1375 | 1403 | 1938 | Node~103088446 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | O. Christian - 10/10/2018 - 2" diameter gum tree leaned over in thick brush 18' off CL contacting line and causing FCB to open. Tree cut /removed and service restored. No damage to conductors, poles or line hardware. ~~~ 10/10/2018 (25 days) ¦ JOCHRIS ¦ Investigative Action
129 | Veg - MED35 | Garner c72037 | ANGIER 230KV - ANGIER 23KV | 9/14/2018 01:22 | 9/14/2018 11:47 | 4821335 | RECLOSER - ABC FID: P420BH_103398784 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | OA Oak | 5 | F2 Forced Outage | 12 Hurricane | 1914 | 2585 | 625 | X948 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None Tree limb at DIS#X948 Tree limb at DIS#X948 | MHS- a 2" in DIA. oak branch broke out of the tree due to high winds. Falling across all 3 phases and locking out the Recloser at P420BH. Crew removed the tree limb and had DCC close the recloser back in. ~~~ 9/26/2018 ¦ c72037 ¦ Investigative Action
130 | Veg - MED35 | Selma e68825 | SELMA 230KV - FIELDCREST 23KV | 9/14/2018 02:39 | 9/15/2018 13:35 | 4818416 | RECLOSER - A C FID: PT62BA_104177336 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LD Tree limb, dead | D2 Dead | NA | PV Pine, Virginia | 30 | F2 Forced Outage | 12 Hurricane | 1549 | 2602 | 2096 | PZ50BA-PZ51BA | Missing Missing Missing | Peel/Fontana 10/4/18: A 1" dia. x 5' long dead limb broke off a 2.5' dia. x ~60' tap Virginia Pine, 30' off of the line CL, was blown/fell onto the feeder in span PZ50BA-PZ51BA, lodged onto A & C phase primary conductors, and locked out A&C phases of G&W recloserPT62BA. No Damage. Crew removed the limb from the line and had the recloser closed back in to restore service. ~~~ 10/4/2018 (19 days) ¦ e68825 ¦ Investigative Action
131 | Veg - MED35 | Garner c72037 | GARNER WHITE OAK 230KV - WHITE OAK 24KV | 9/14/2018 02:48 | 9/14/2018 13:20 | 4818349 | OCB - ABC FID: T4730B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LX Trees, overgrown primary | DN No apparent defect | NA | MG Magnolia | 0 | F2 Forced Outage | 12 Hurricane | 1878 | 1908 | 632 | X845 | Overhead Fac Undetermined Feeder Circuit Breaker Lockout Unable to find a fault | MHS-found Magnolia burning into primary wire at X845 using CYME and FMS to find location belive this is were wind was blowing tree into primary taking out FCB ~~~ 10/4/2018 (20 days) ¦ c72037 ¦ Investigative Action
132 | Veg - MED35 | Henderson omshistproc | HENDERSON 230KV - HENDERSON WEST 24KV | 9/14/2018 02:51 | 9/14/2018 08:08 | 4818355 | OCB - ABC FID: T4790B16 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1311 | 1336 | 317 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
133 | Veg - MED35 | Raleigh DFontan | NEUSE 115KV - POSSUM TRACK 23KV | 9/14/2018 03:48 | 9/14/2018 08:46 | 4818399 | RECLOSER - BC FID: HF66BK_103509896 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DV Visible stem decay | NA | SZ Sweet Gum | 16 | F2 Forced Outage | 12 Hurricane | 511 | 837 | 298 | HF70BK TO HF71BK | Tree/Vegetatn Limb Fell from Inside Right of Way None found limb on line FAULT APPEARS TO BE JUST BEYOND RECLOSER 0C08BK | Fontana 9/27/18 - 2" by 15' long live limb broke off a 1' by 70' tall sweet gum located 16 feet of the feeder center line. The limb fell out into the feeder between span HF70 and HF71, lodged into the primary and locked out B & C phase of recloser HF66BK. Crews had to open up A phase of the recloser to safely remove the limb from the line. NO DAMAGE (Hurricane Florence) ~~~ 9/27/2018 ¦ DFontan ¦ Investigative Action
134 | Veg - MED35 | Selma omshistproc | WILSON MILLS 230KV - WILSON MILLS 24KV | 9/14/2018 04:00 | 9/14/2018 09:25 | 4819305 | RECLOSER - ABC FID: 5HC08_104526452 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 512 | 2102 | 325 | Recloser~5HC08_104526452 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None trees trees | ... NO OUTAGE REVIEW INFO
135 | Veg - MED35 | Cary JOCHRIS | AMBERLY 230KV - CAROLINA PRESERVE 24KV | 9/14/2018 04:37 | 9/14/2018 14:42 | 4819454-2 | SWITCH - ABC FID: 12M700_104473895 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | 47 Replaced Pole | P2 Pole, CCA | SZ Sweet Gum | 5 | F2 Forced Outage | 03 Wind | 2727 | 3865 | 605 | Line~15AM52_15AM51_113636670 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree on primary @ 15AM53 | O. Christian - 10/8/2018 - 24" diameter gum tree 5' off CL split 7' above ground level and fell breaking 55C3 CCA vertical angle pole 15AM53 causing the outage of 2727 customers. New pole set and service restored. This was definitely a danger tree that should have been taken down previously. ~~~ 10/8/2018 (24 days) ¦ JOCHRIS ¦ Investigative Action
136 | Veg - MED35 | Cary JOCHRIS | AMBERLY 230KV - CAROLINA PRESERVE 24KV | 9/14/2018 04:37 | 9/14/2018 09:31 | 4819454-1 | OCB - ABC FID: T4604B10 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | 47 Replaced Pole | P2 Pole, CCA | SZ Sweet Gum | 5 | F2 Forced Outage | 03 Wind | 544 | 3865 | 294 | Line~15AM52_15AM51_113636670 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree on primary @ 15AM53 | O. Christian - 10/8/2018 - 24" diameter gum tree 5' off CL split 7' above ground level and fell breaking 55C3 CCA vertical angle pole 15AM53 causing the outage of 2727 customers. New pole set and service restored. This was definitely a danger tree that should have been taken down previously. ~~~ 10/8/2018 (24 days) ¦ JOCHRIS ¦ Investigative Action
137 | Veg - MED35 | Zebulon i70604 | SPRING HOPE 115KV - TAYLORS CROSSROADS 23KV | 9/14/2018 04:49 | 9/14/2018 09:21 | 4821940 | OCB - ABC FID: T6041B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TP Tree fails, partial | DX Other defect | 29 Conductor, bare | MR Maple, red |  | F2 Forced Outage | 12 Hurricane | 2050 | 2058 | 272 |  | Tree/Vegetatn Limb Fell from Outside Right of Way None s 6A ALT NEAR PRISON DIS# BR00BC ONE PHASE DOWN ON THREE PHASE LINE | CPS// Defective maple tree top broke and fell on conductor near dis#BR00BC causing the circuit breaker to open // Responding Service Tech and crew made repairs to #2 BC and circuit was re-energized // Damage to equipment included one phase of #2 BC // Unable to measure distance from wire to where tree top broke out ~~~ 9/24/2018 ¦ i70604 ¦ Investigative Action
138 | Veg - MED35 | Zebulon i70604 | ARCHER LODGE 230KV - THANKSGIVING FIRE ROAD 24KV | 9/14/2018 05:15 | 9/14/2018 10:05 | 4819757 | OCB - ABC FID: T4500B23 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 26 Vines | D2 Dead | 29 Conductor, bare | KZ Kudzu |  | F2 Forced Outage | 12 Hurricane | 1139 | 1138 | 290 | 18TY59 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | CPS// Dead pine tree top, covered with vines, broke and fell on conductor causing circuit breaker to open // Tree was located near dis#18TY59 // Responding line techs waited for Hurricane winds to subside and removed the vines as well as the tree top from the line // Vegetation WR was generated (see below) // 477 conductor was damaged and will be repaired ~~~ 9/24/2018 ¦ i70604 ¦ Vegetation Management
139 | Veg - MED35 | Garner c72037 | GARNER 115KV - GARNER 24KV | 9/14/2018 05:17 | 9/14/2018 13:24 | 4822173 | OCB - ABC FID: T4720B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LL Tree limb fails | 37 Removed Limb or Tree From Lin | NA | PC Pecan | 5 | F2 Forced Outage | 12 Hurricane | 1188 | 1291 | 487 | DK89BJ | Overhead Fac Undetermined FCB Lockout Under Hot Line Tag (Comments) WIND? DA team assigned, Travis Williams. LINE WAS CLEAR AROUND 11AM 9/14 | MHS- Talking with service man,while line was under hot line tag a pecan tree limb broke and blew into feeder at DIS# DK89BJ locking out the FCB. crew cleared branch and had DCC re-energize the FCB. no pics yard was cleaned up when I got there ~~~ 10/4/2018 (20 days) ¦ c72037 ¦ Investigative Action
140 | Veg - MED35 | Zebulon i70604 | ZEBULON 115KV - ZEBULON EAST 23KV | 9/14/2018 05:51 | 9/14/2018 10:16 | 4820177 | OCB - ABC FID: T6090B06 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | B1 Brace | SZ Sweet Gum | 61 | F2 Forced Outage | 12 Hurricane | 1210 | 1234 | 265 | A773BF | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None gum tree | CPS// Defective sweet gum tree located 61' from center line near dis#A773BF fell and contacted conductor causing the circuit breaker to open // Responding service techs removed tree from line with the aid of a tree crew and the circuit breaker was re-energized// Damage to equipment included a broken cross arm brace // No other equipment was damaged ~~~ 9/24/2018 ¦ i70604 ¦ Work Order(s) Generated
141 | Veg - MED35 | Sanford i25781 | BEAR BRANCH 230KV - BENHAVEN 24KV | 9/14/2018 05:57 | 9/14/2018 09:16 | 4820275 | OCB - ABC FID: T2443B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DD Co-dominate stem | NA | OA Oak | 17 | F2 Forced Outage | 17 Wind and Rain | 1552 | 1566 | 199 | Line~1B0R84_K550AC_108792739 | Tree/Vegetatn Limb Fell from Outside Right of Way None HURRICAN FLORENCE | JWW// On 9/14/18 at 05:57 during hurricane Florence an Oak tree fell from outside of the right of way on the three phase at K550AC locking out the Benhaven FDR and causing 1552 customers to lose power. When service tech arrived he cut tree off and had DCC energize the FDR at 09:16 restoring power to all 1552 customers. No damage to conductor. ~~~ 9/26/2018 ¦ i25781 ¦ Investigative Action
142 | Veg - MED35 | Durham AArias | ENO - 14102402 | 9/14/2018 05:57 | 9/14/2018 07:18 | 10901481 | S-RCL - ABC Size: 800 VPST FID: 38998801 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | 43 Recloser, Electronic | OA Oak | 20 | F2 Forced Outage | 12 Hurricane | 1067 | 2012 | 81 | Intersection of Bennett Memorial and Neal Rd. | CMPL 2018-09-14 07:21:00 by SCHAMBE RMK: RECLOSER LOCK OUT | aarias// MED - hurricane in area. Dead oak limb fell from outside ROW (20 ft) on double ckt line across 2 phases. Removed limb and and re-energized electronic recloser. ~~~ 9/21/2018 ¦ AArias ¦ Investigative Action
143 | Veg - MED35 | Sanford omshistproc | SANFORD GARDEN STREET - WOODLAND AVENUE 23KV | 9/14/2018 06:09 | 9/15/2018 14:12 | 4837078 | OCB - ABC FID: T2432B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 2253 | 2966 | 1923 | Line~0500AC_0495AC_2439626 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE FELL ON LINE T911 TICKET 12498185 -- RONALD GREGORY - MASTEC | ... NO OUTAGE REVIEW INFO
144 | Veg - MED35 | Garner c72037 | GARNER WHITE OAK 230KV - CORNWALLIS 24KV | 9/14/2018 06:13 | 9/15/2018 17:56 | 4820439 | OCB - ABC FID: T4730B11 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | P2 Pole, CCA | PT PINE | 30 | F2 Forced Outage | 12 Hurricane | 2,082 Cust Eq: 1621 | 1923 | 2143 | GG23BJ | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None Broke pole at GG21BJ. on Bull horns will work back. Trans will work back 25KVA. Re sag Tap line going down Old Cascade Dr. | MHS- A defective pine tree about 2' in DIA. broke about 6' above ground level and 30' from C/L, falling across all 3 phases breaking top out of pole at DIS# GG21BJ ~~~ 9/28/2018 ¦ c72037 ¦ Investigative Action
145 | Veg - MED35 | Garner c72037 | AUBURN 230KV - ROCK QUARRY ROAD 23KV | 9/14/2018 06:20 | 9/14/2018 20:45 | 4820519-2 | OCB - ABC FID: T4501B01 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | 29 Conductor, bare | OA Oak | 18 | F2 Forced Outage | 12 Hurricane | 529 | 2669 | 865 | ED07BJ | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None 477 down, 6620 Battlebridge Rd | MHS- A dead 4" in DIA. Oak branch broke out of the tree about 45' up and 18' from C/L falling across B&C phases burning c phase to the ground. Which opened recloser at EC15BJ. crew repaired and DCC hotted back up. ~~~ 9/26/2018 ¦ c72037 ¦ Investigative Action
146 | Veg - MED35 | Garner c72037 | AUBURN 230KV - ROCK QUARRY ROAD 23KV | 9/14/2018 06:20 | 9/14/2018 10:43 | 4820519-1 | RECLOSER - ABC FID: EC15BJ_104362554 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | 29 Conductor, bare | OA Oak | 18 | F2 Forced Outage | 12 Hurricane | 937 | 2669 | 263 | ED07BJ | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None 477 down, 6620 Battlebridge Rd | MHS- A dead 4" in DIA. Oak branch broke out of the tree about 45' up and 18' from C/L falling across B&C phases burning c phase to the ground. Which opened recloser at EC15BJ. crew repaired and DCC hotted back up. ~~~ 9/26/2018 ¦ c72037 ¦ Investigative Action
147 | Veg - MED35 | Garner c72037 | GARNER I-40 230KV - BARWELL ROAD 24KV | 9/14/2018 06:34 | 9/15/2018 19:53 | 4832454 | OCB - ABC FID: T4723B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | PT PINE | 9 | F2 Forced Outage | 12 Hurricane | 2295 | 2312 | 2239 | EF32BJ | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None fuse open at EG09BJ, 3 pines on tapline DA team confirmed 5:30pm, 9-15-18. - J Snow | MHS- a Pine tree about 2' in DIA. and 9' from C/L fell and broke tap line which sprung back up and around feeder locking out the FCB ~~~ 9/26/2018 ¦ c72037 ¦ Investigative Action
148 | Veg - MED35 | Garner c72037 | CLAYTON 115KV - BARBER MILL 24KV | 9/14/2018 06:36 | 9/15/2018 10:00 | 4825589 | OCB - ABC FID: T5640B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | UU Unknown Manufacturer | 5 | F2 Forced Outage | 12 Hurricane | 2103 | 2523 | 1644 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree on wire | MHS- Ran CYME and FMS. rode out locations could not find anything in area. no pics no outage review. ~~~ 10/4/2018 (19 days) ¦ c72037 ¦ Investigative Action
149 | Veg - MED35 | Garner c72037 | CLAYTON 115KV - GLENHAVEN 24KV | 9/14/2018 06:53 | 9/14/2018 17:03 | 4823999 | OCB - ABC FID: T5640B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | P1 Pole, Creosote | OR Oak, red | 75 | F2 Forced Outage | 12 Hurricane | 1452 | 1465 | 610 | JV25BJ | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None broke pole | MHS- A Red oak tree about 36" in DIA. and 75' from C/L fell across line at JV25BJ Breaking the pole. it also broke 2 more poles up from it at DIS# JV01BJ and JV02BJ. the tree was in wet area with stream running beside it. roots were shallow. ~~~ 9/26/2018 ¦ c72037 ¦ Investigative Action
150 | Veg - MED35 | Garner c72037 | ANGIER 230KV - PEARIDGE 23KV | 9/14/2018 06:53 | 9/14/2018 08:59 | 4820904 | RECLOSER - BC FID: P762BH_104370309 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LH Tree limb, overhang | DN No apparent defect | NA | SZ Sweet Gum | 0 | F2 Forced Outage | 12 Hurricane | 1020 | 2410 | 126 | P783BH | Missing Missing Missing | MHS- a 1" in DIA. live sweet gum tree branch broke out of tree at DIS# P783BH and fell across all 3 phases locking out recloser P762BH Crew removed branch and had DCC reenergize recloser. ~~~ 9/26/2018 ¦ c72037 ¦ Investigative Action
151 | Veg - MED35 | Asheboro omshistproc | ASHEBORO SOUTH 115KV - MCDOWELL ROAD 23KV | 9/14/2018 06:58 | 9/14/2018 07:42 | 4820975-2 | OCB - ABC FID: T0950B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 887 | 1445 | 44 |  | Tree/Vegetatn Limb Fell from Outside Right of Way None tree limb at dis # pmz21 tree limb at dis # pmz21 | ... NO OUTAGE REVIEW INFO
152 | Veg - MED35 | Raleigh DFontan | RALEIGH YONKERS ROAD 115KV - CRABTREE CREEK 24KV | 9/14/2018 07:00 | 9/14/2018 09:16 | 4820992 | RECLOSER - XZ FID: 0C08BK_104336296 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LL Tree limb fails | DN No apparent defect | NA | OW Oak, willow | 28 | F2 Forced Outage | 12 Hurricane | 1304 | 2151 | 136 | RDS00-RDS32 | Missing Missing Missing FAULT APPEARS TO BE BETWEEN RDS00-RDR3 OR BETWEEN RDR44-RDQ32 | Peel/Fontana 9/27/18 - A 3/4" diameter by 4' long live branch from a 3' diameter by 70' tall Willow Oak28' off of line CL broke and fell onto the primary conductors in span RDS00-RDS32, locking out A & C phases of the recloser. NO DAMAGE (Hurricane Florence) ~~~ 9/27/2018 ¦ DFontan ¦ Investigative Action
153 | Veg - MED35 | Cary JOCHRIS | RALEIGH SOUTH 115KV - LAKE DAM 23KV | 9/14/2018 07:08 | 9/14/2018 09:39 | 4821070 | RECLOSER - BC FID: 17H197_104157003 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LL Tree limb fails | 37 Removed Limb or Tree From Lin | NA | OB Oak, white |  | F2 Forced Outage | 03 Wind | 1199 | 2978 | 151 | Recloser~17H197_104157003 | Overhead Fac Undetermined Recloser Lockout Tree limb on line at 17H197 | O. Christian - 10/9/2018 - 2" diameter live oak tree limb contacted line causing recloser 17H197 to open taking out 1199 customers during hurricane. Unable to determine where limb originated. ~~~ 10/9/2018 (25 days) ¦ JOCHRIS ¦ Investigative Action
154 | Veg - MED35 | Garner c72037 | GARNER TRYON HILLS 115KV - YEARGAN ROAD 24KV | 9/14/2018 07:31 | 9/14/2018 14:03 | 4826329 | OCB - ABC FID: T5314B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TF Tree fails, defective | DE Erosion/poor enviornment | 48 Transformer | OR Oak, red | 30 | F2 Forced Outage | 12 Hurricane | 1753 | 1883 | 392 | NG99BJ | Missing Missing Missing | MHS- A defective 12" Red oak fell about 30' from C/L and at ground level. also in a drain ditch, pulling several other small trees down because of vines wrapped around them. they fell into the primary locking out the FCB. crews cut trees back from primary . crew had to replace transformer and cutout. crew had DCC reenergize FCB after repairs were done ~~~ 10/4/2018 (20 days) ¦ c72037 ¦ Investigative Action
155 | Veg - MED35 | Garner c72037 | GARNER PANTHER BRANCH 230KV - WILLIAMS CROSSROADS 24KV | 9/14/2018 07:33 | 9/14/2018 11:40 | 4823510 | OCB - ABC FID: T4725B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin | NA | PC Pecan | 0 | F2 Forced Outage | 12 Hurricane | 1652 | 1699 | 247 | T913BJ | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None t913bj | MHS- A 1" in DIA. live Pecan tree branch broke out of tree falling across all 3 phases locking out FCB. Crew removed limb and had DCC hot the breaker back up ~~~ 9/28/2018 ¦ c72037 ¦ Investigative Action
156 | Veg - MED35 | Garner omshistproc | MILBURNIE 230KV - BELTLINE 23KV | 9/14/2018 07:35 | 9/14/2018 11:50 | 4823695 | OCB - ABC FID: T5000B44 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 03 Wind | 1099 | 1100 | 255 | Node~2070656 | Tree/Vegetatn Tree/Limb Growth None tree limb tree limb | ... NO OUTAGE REVIEW INFO
157 | Veg - MED35 | Sanford i25781 | SANFORD HORNER BLVD. 230KV - GULF 23KV | 9/14/2018 07:42 | 9/14/2018 09:23 | 4821464 | OCB - ABC FID: T2440B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | OA Oak | 17 | F2 Forced Outage | 17 Wind and Rain | 1726 | 1839 | 101 | Line~Q677AC_Q678AC_2460895 | Tree/Vegetatn Limb Fell from Outside Right of Way None | JWW// On 9/14/18 at 07:42 during hurricane Florence a small oak tree from outside of the right of way fell on the three phase locking out the Gulf feeder causing 1726 customers to lose power. When the service tech arrived he cut tree off of the three phase and had DCC energize the feeder at 09:23 restoring power to all customers. No damage done to conductor. ~~~ 9/26/2018 ¦ i25781 ¦ Investigative Action
158 | Veg - MED35 | Cary c72037 | FUQUAY BELLS LAKE 230KV - STATE ROAD 1010 23KV | 9/14/2018 07:50 | 9/14/2018 11:07 | 4822007 | RECLOSER - A C FID: 100795_104307157 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 03 Tree (Vegetation) | 37 Removed Limb or Tree From Lin | NA | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 683 | 1932 | 197 | 7417K | Overhead Fac Undetermined Recloser Lockout Limb on lines between 17WQ57 and 7417K DA TEAM ASSIGNED - MCLAUGHLIN////LIMB ON LINE BETWEEN 17WQ57 AND 7417K | MHS- limb on line between DIS# 17WQ57 and 7417K, crew removed limb and had DCC reenergize the recloser. limb was cleaned up when I went to look. no pics or outage review ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Investigative Action
159 | Veg - MED35 | Cary JOCHRIS | APEX 230KV - APEX NORTH 23KV | 9/14/2018 08:40 | 9/14/2018 09:35 | 4822737 | OCB - ABC FID: T4530B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TF Tree fails, defective | 37 Removed Limb or Tree From Lin | NA | PW Pine, white | 19 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1473 | 1294 | 55 | 6477K-6479K | Missing Missing Missing | O. Christian - 10/10/2018 - 2" diameter live white pine tree 19' off CL broke off 2' above ground contacting line and causing the outage of the FCB and outage of 1473 customers. No damage to conductors, poles or pole line hardware. Double circuit line with the Southchase 23KV FDR and the Apex North 23KV FDR. ~~~ 10/10/2018 (26 days) ¦ JOCHRIS ¦ Investigative Action
160 | Veg - MED35 | Selma e68825 | FOUR OAKS 230KV - HOLTS LAKE 24KV | 9/14/2018 08:47 | 9/14/2018 11:35 | 4822483 | RECLOSER - ABC FID: U939_103866788 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | PL Pine, loblolly | 65 | F2 Forced Outage | 12 Hurricane | 1757 | 2897 | 168 | U775-U779 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | Peel/Fontana 10/4/18: A 1.5" dia. x 8' long live limb broke out of the top of a 6' dia. x ~75' tall Loblolly Pine, 65' off of the line CL, landed on the feeder in span U775-U779, lodged into the primary conductors, and locked out all 3 phases of G&W recloser U939. No damage. Crew removed the limb, and had the reclosed closed back in to restore service. ~~~ 10/4/2018 (20 days) ¦ e68825 ¦ Investigative Action
161 | Veg - MED35 | Raleigh omshistproc | RALEIGH FOXCROFT 230KV - SOUTH HALL 23KV | 9/14/2018 09:12 | 9/14/2018 10:15 | 4822507 | OCB - ABC FID: T4692B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 999 | 2742 | 63 | Line~HB39BK_7GQ40_1209326 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
162 | Veg - MED35 | Garner c72037 | ANGIER 230KV - PEARIDGE 23KV | 9/14/2018 09:13 | 9/14/2018 12:56 | 4822711 | RECLOSER - BC FID: P762BH_104370309 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | LX Trees, overgrown primary | DN No apparent defect | NA | SZ Sweet Gum | 0 | F2 Forced Outage | 12 Hurricane | 1020 | 2410 | 223 | P783BH | Missing Missing Missing | MHS- a 1" in DIA. live sweet gum tree branch broke out of tree at DIS# P783BH and fell across all 3 phases locking out recloser P762BH Crew removed branch and had DCC reenergize recloser. ~~~ 9/26/2018 ¦ c72037 ¦ Investigative Action
163 | Veg - MED35 | Cary JOCHRIS | CARY 230KV - CHAPEL HILL ROAD 23KV | 9/14/2018 09:16 | 9/14/2018 12:15 | 4822548 | RECLOSER - XYZ FID: R060K_2779727 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | PW Pine, white | 0 | F2 Forced Outage | 03 Wind | 1876 | 3434 | 179 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None 4822548 DA team assigned, Josh Ferguson | O. Christian - 10/11/2018 - Small live pine tree limb on line at B549K causing recloser R060K to open. Undetermined where limb came. No carbon tracks or burn marks detected. ~~~ 10/11/2018 (27 days) ¦ JOCHRIS ¦ Investigative Action
164 | Veg - MED35 | Cary omshistproc | CARY 230KV - CHAPEL HILL ROAD 23KV | 9/14/2018 09:20 | 9/14/2018 12:15 | 4822828 | RECLOSER - B FID: R060K_2779727 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | EA R Major Storm | 981 | 3434 | 175 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
165 | Veg - MED35 | Sanford omshistproc | SANFORD HORNER BLVD. 230KV - GULF 23KV | 9/14/2018 09:25 | 9/14/2018 11:00 | 4823820 | OCB - ABC FID: T2440B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1730 | 1839 | 95 |  | Tree/Vegetatn Limb Fell from Outside Right of Way None | ... NO OUTAGE REVIEW INFO
166 | Veg - MED35 | Cary JOCHRIS | CARY REGENCY PARK 230KV - SOUTHCHASE 23KV | 9/14/2018 09:34 | 9/14/2018 12:38 | 4822776 | OCB - ABC FID: T4599B24 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TF Tree fails, defective | 37 Removed Limb or Tree From Lin | NA | PW Pine, white | 19 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1538 | 1476 | 184 | 6477K-6479K | Overhead Fac Undetermined Feeder Circuit Breaker Lockout South Chase feeder lockout DA team assigned, Niko Johnson | O. Christian - 10/10/2018 - 2" diameter live white pine tree 19' off CL broke off 2' above ground contacting line and causing the outage of the FCB and outage of 1473 customers. No damage to conductors, poles or pole line hardware. Double circuit line with the Southchase 23KV FDR and the Apex North 23KV FDR. ~~~ 10/10/2018 (26 days) ¦ JOCHRIS ¦ Investigative Action
167 | Veg - MED35 | Cary JOCHRIS | APEX 230KV - APEX NORTH 23KV | 9/14/2018 09:37 | 9/14/2018 15:02 | 4822777 | OCB - ABC FID: T4530B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TF Tree fails, defective | 37 Removed Limb or Tree From Lin | NA | PW Pine, white | 19 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1473 | 1294 | 325 | Line~6477K_6479K_2625974 | Overhead Fac Undetermined Feeder Circuit Breaker Lockout UNKNOWN | O. Christian - 10/10/2018 - 2" diameter live white pine tree 19' off CL broke off 2' above ground contacting line and causing the outage of the FCB and outage of 1473 customers. No damage to conductors, poles or pole line hardware. Double circuit line with the Southchase 23KV FDR and the Apex North 23KV FDR. ~~~ 10/10/2018 (26 days) ¦ JOCHRIS ¦ Investigative Action
168 | Veg - MED35 | Garner c72037 | HOLLY SPRINGS 230KV - ARBOR CREEK 24KV | 9/14/2018 09:41 | 9/14/2018 15:56 | 4822792-2 | SWITCH - ABC FID: 141D28_2678614 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | 29 Conductor, bare | MP Maple | 0 | F2 Forced Outage | 12 Hurricane | 1475 | 1496 | 375 | 100458 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell on line at 100458 tree fell on line at 100458 | MHS- spoke with service tech, he said that a tree limb fall across double circuit feeder pole locking out both FCB's. Had 1 phase of 477 burn to the ground. crew did switching to get the FCB's back hot. went to look at but home owner had already cleaned up. could not find branch ~~~ 10/4/2018 (20 days) ¦ c72037 ¦ Investigative Action
169 | Veg - MED35 | Chapel Hill AArias | HILLSBOROUGH - 19081201 | 9/14/2018 09:43 | 9/14/2018 22:32 | 109039122 | S-CKT - ABC Size: Class 1A FID: 38359125 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | P1 Pole, Creosote | OA Oak | 55 | F2 Forced Outage | 12 Hurricane | 2030 | 2029 | 769 | aarias// 408 Calvin St | LOCK OUT, POSSIBLE FAULT LOCATION BACK LINE DOUBLE CIRCUIT BETWEEN CALVIN ST AND THE STATION EXIT.tx feeds switching station, 3 PH LINE DOWN AT REX DRIVE AND DIMMOCKS MILL RD PER TRANSMISSION TECH. KEVIN SHAMBLEY/919-201-4358 | aarias// MED - hurricane in area. Diseased oak tree (largest tree in the town of Hillsborough) fell from 55 ft away across the street in front of 408 Calvin St on double pole line for Hillsborough 1201 (tkt 109039122) and Hillsborough 1202 (tkt 109039121). Visual inspection of tree revealed internal stem decay. Damaged 2 45' poles, 1 30' pole, primary wire on both circuits, and several crossarms across 6 spans of primary. Jumpers were cut and a set of Solid Blades (FACID 39041276) was closed to isolate damage and backfeed most of 1201 from 1202. Solid blades and 1202 breaker (tkts 10904965 & 10904904) open to restore feed to normal. ~~~ 9/14/2018 ¦ AArias ¦ Investigative Action
170 | Veg - MED35 | Chapel Hill AArias | HILLSBOROUGH - 19081202 | 9/14/2018 09:43 | 9/14/2018 19:16 | 109039121 | S-CKT - ABC Size: Class 1 FID: 38359317 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | PP Pole | OA Oak | 55 | F2 Forced Outage | 12 Hurricane | 1449 | 1457 | 573 |  | LOCK OUT, POSSIBLE FAULT LOCATION BACK LINE DOUBLE CIRCUIT BETWEEN CALVIN ST AND THE STATION EXIT.tx feeds switching station, 3 PH LINE DOWN AT REX DRIVE AND DIMMOCKS MILL RD PER TRANSMISSION TECH. KEVIN SHAMBLEY/919-201-4358 | aarias// MED - hurricane in area. Diseased oak tree (largest tree in the town of Hillsborough) fell from 55 ft away across the street in front of 408 Calvin St on double pole line for Hillsborough 1201 (tkt 109039122) and Hillsborough 1202 (tkt 109039121). Visual inspection of tree revealed internal stem decay. Damaged 2 45' poles, 1 30' pole, primary wire on both circuits, and several crossarms across 6 spans of primary. Jumpers were cut and a set of Solid Blades (FACID 39041276) was closed to isolate damage and backfeed most of 1201 from 1202. Solid blades and 1202 breaker (tkts 10904965 & 10904904) open to restore feed to normal. ~~~ 9/14/2018 ¦ AArias ¦ Investigative Action
171 | Veg - MED35 | Garner c72037 | HOLLY SPRINGS 230KV - FELTONSVILLE 24KV | 9/14/2018 09:45 | 9/14/2018 13:41 | 4822838-1 | OCB - ABC FID: T4795B23 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | 29 Conductor, bare | MP Maple | 0 | F2 Forced Outage | 12 Hurricane | 2667 | 3454 | 236 | 100458 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell on line at 100458 tree fell on line at 100458 | MHS- spoke with service tech, he said that a tree limb fall across double circuit feeder pole locking out both FCB's. Had 1 phase of 477 burn to the ground. crew did switching to get the FCB's back hot. went to look at but home owner had already cleaned up. could not find branch ~~~ 10/4/2018 (20 days) ¦ c72037 ¦ Investigative Action
172 | Veg - MED35 | Chatham County omshistproc | SILER CITY 115KV - SILER CITY NORTH 24KV | 9/14/2018 09:48 | 9/14/2018 13:39 | 4823372-2 | SWITCH - ABC FID: 3959AF_2394910 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 544 | 2576 | 232 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree at 3987af tree at 3987af | ... NO OUTAGE REVIEW INFO
173 | Veg - MED35 | Selma omshistproc | WILSON MILLS 230KV - WILSON MILLS 24KV | 9/14/2018 09:48 | 9/14/2018 15:00 | 4822911 | RECLOSER - ABC FID: 17Y536_104527583 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 632 | 2102 | 311 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None trees trees | ... NO OUTAGE REVIEW INFO
174 | Veg - MED35 | Selma omshistproc | WILSON MILLS 230KV - WEST SMITHFIELD 24KV | 9/14/2018 09:57 | 9/15/2018 13:45 | 4833912 | OCB - ABC FID: T5385B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 900 | 1867 | 1668 |  | Tree/Vegetatn Tree/Limb Growth None trees trees | ... NO OUTAGE REVIEW INFO
175 | Veg - MED35 | Zebulon i70604 | ARCHER LODGE 230KV - RIVER DELL 24KV | 9/14/2018 10:04 | 9/14/2018 11:58 | 4823097 | OCB - ABC FID: T4500B10 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | NA | PT PINE | 24 | F2 Forced Outage | 12 Hurricane | 1916 | 2074 | 114 | 1BQK77 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None OPENED AT 105R21 | CPS// Defective pine tree fell across double circuit at dis# 1BQK77 causing both the Flowers and the River Dell circuit breakers to open // tree was located 24' from center line // Responding Service tech had tree resources to remove tree from line and both circuits were re-energized // No damage to equipment // Hurricane ~~~ 9/24/2018 ¦ i70604 ¦ Investigative Action
176 | Veg - MED35 | Zebulon i70604 | ARCHER LODGE 230KV - FLOWERS 24KV | 9/14/2018 10:04 | 9/14/2018 11:57 | 4823053 | OCB - ABC FID: T4500B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DV Visible stem decay | NA | PT PINE | 24 | F2 Forced Outage | 12 Hurricane | 2125 | 2260 | 113 | 1BQK77 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None OPENED AT 1CBH30 OPENED AT 1CBH30 | CPS// Defective pine tree fell across double circuit at dis# 1BQK77 causing both the Flowers and the River Dell circuit breakers to open // tree was located 24' from center line // Responding Service tech had tree resources to remove tree from line and both circuits were re-energized // No damage to equipment // Hurricane ~~~ 9/24/2018 ¦ i70604 ¦ Investigative Action
177 | Veg - MED35 | Chatham County omshistproc | SILER CITY 115KV - SNOW CAMP ROAD 24KV | 9/14/2018 10:15 | 9/15/2018 17:33 | 4823184-3 | RECLOSER - ABC FID: 0523AF_2361163 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 923 | 1395 | 1878 | Node~1278119 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree has 3 phases down at 0653AF--energized up to SBD at 0647AF tree has 3 phases down at 0653AF--energized up to SBD at 0647AF | ... NO OUTAGE REVIEW INFO
178 | Veg - MED35 | Zebulon omshistproc | CASTALIA 230KV - HOLLISTER 24KV | 9/14/2018 10:17 | 9/14/2018 14:55 | 4823223 | RECLOSER - ABC FID: CK37BC_1949211 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 622 | 1675 | 278 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Tree fell brushing primary knocking b phase off the insulator at CK76BC and knocking c phase off insulator at WC46BC locking Tree fell brushing primary knocking b phase off the insulator at CK76BC and knocking c phase off insulator at WC46BC locking out three pole top reclosers at CK37BC | ... NO OUTAGE REVIEW INFO
179 | Veg - MED35 | Raleigh DFontan | RALEIGH BLUE RIDGE 230KV - GLENWOOD AVENUE 23KV | 9/14/2018 10:27 | 9/14/2018 13:00 | 4824128 | OCB - ABC FID: T5122B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | NA | MV Maple, silver | 12 | F2 Forced Outage | 12 Hurricane | 1882 | 1857 | 153 | LH20BL | Tree/Vegetatn Limb Fell from Outside Right of Way None tree limb at lh20bl | Peel/Fontana 9/27/18 - 1" by 4' long live limb broke off a 2.5' by 70' tall silver maple 12' off of the line CL, and fell onto the feeder at pole LH20BL, locking out the FCB. The tree was overhanging the line. NO DAMAGE (Hurricane Florence) ~~~ 9/27/2018 ¦ DFontan ¦ Investigative Action
180 | Veg - MED35 | Garner c72037 | CLAYTON 115KV - TV 24KV | 9/14/2018 11:03 | 9/14/2018 19:40 | 4823770-3 | SWITCH - ABC FID: 13G001_1677394 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | SZ Sweet Gum | 18 | F2 Forced Outage | 12 Hurricane | 669 | 1916 | 517 | NH67 | Missing Missing Missing | MHS-a 12" in DIA. live sweet gum tree fell from ground level about 18' from C/L across all 3 phases locking out the T.V. FCB. crew opened up airbreak switch 13G001 then had DCC reenergize the FCB getting 457 customers back on. they then opened up GW GF72BJ and closed in air break switch G0467 getting another 716 customers back on the remaining 669 had to stay off till the tree was removed ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Investigative Action
181 | Veg - MED35 | Garner c72037 | CLAYTON 115KV - TV 24KV | 9/14/2018 11:03 | 9/14/2018 13:12 | 4823770-1 | SWITCH - ABC FID: G0467_103727804 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | SZ Sweet Gum | 18 | F2 Forced Outage | 12 Hurricane | 716 | 1916 | 129 | NH67 | Missing Missing Missing | MHS-a 12" in DIA. live sweet gum tree fell from ground level about 18' from C/L across all 3 phases locking out the T.V. FCB. crew opened up airbreak switch 13G001 then had DCC reenergize the FCB getting 457 customers back on. they then opened up GW GF72BJ and closed in air break switch G0467 getting another 716 customers back on the remaining 669 had to stay off till the tree was removed ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Investigative Action
182 | Veg - MED35 | Garner c72037 | MILBURNIE 230KV - WILDERS GROVE 23KV | 9/14/2018 11:06 | 9/14/2018 14:17 | 4823754 | RECLOSER - BC FID: GT69BJ_104342196 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | UU Unknown Manufacturer | 30 | F2 Forced Outage | 12 Hurricane | 2733 | 2517 | 191 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | MHS- Tree fell from outside or right of way. ran CYME and FMS rode line out found nothing, no pics or outage review ~~~ 10/4/2018 (20 days) ¦ c72037 ¦ Investigative Action
183 | Veg - MED35 | Roxboro omshistproc | BAHAMA 230KV - ROUGEMONT 23KV | 9/14/2018 11:21 | 9/14/2018 13:52 | 4823961 | RECLOSER - A C FID: E1217_2580721 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1413 | 1906 | 151 | Load~10G647 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE ON PRIMARY CAUSED PHASE TO BURN DOWN AT E1L37 | ... NO OUTAGE REVIEW INFO
184 | Veg - MED35 | Zebulon omshistproc | ROLESVILLE 230KV - MITCHELL MILL 24KV | 9/14/2018 11:23 | 9/14/2018 18:57 | 4829403 | RECLOSER - ABC FID: 1AXT88_110805894 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 03 Wind | 919 | 1958 | 454 | Node~103847033 | Tree/Vegetatn Tree/Limb Growth None limb got into feeder limb got into feeder | ... NO OUTAGE REVIEW INFO
185 | Veg - MED35 | Henderson i67431 | WARRENTON 115KV - HIGHWAY 401 NORTH 23KV | 9/14/2018 12:05 | 9/14/2018 17:35 | 4824530 | RECLOSER - BC FID: EAU47_1878163 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect |  | UU Unknown Manufacturer | 25 | F2 Forced Outage | 03 Wind | 619 | 1697 | 330 |  | Tree/Vegetatn Limb Fell from Outside Right of Way None ABB switch is opn at EAU47 due to tree on primary at EAU90 ABB switch is opn at EAU47 due to tree on primary at EAU90 | DPW: Verified coding ~~~ 9/17/2018 ¦ i67431 ¦ Completion Codes or Remarks
186 | Veg - MED35 | Durham AArias | GARRETT RD - 14202411 | 9/14/2018 12:13 | 9/14/2018 13:05 | 10902537 | S-CKT - ABC Size: Class 1A FID: 38355885 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | PT PINE | 30 | F2 Forced Outage | 12 Hurricane | 1195 | 2890 | 52 | 4705 Old Chapel Hill Rd | CIRCUIT LOCKOUT. TARGETS A-B-C. FMAG 3986 LARGE PINE @ BUCHANAN DR & OLD CHAPEL HILL RD. RECLOSER FID 38998805 ALSO LOCKED OUT | aarias// MED - hurricane. Recloser locked out (tkt 10902535) due to a live pine tree that broke near the base and fell across all 3 phases from 30' away directly across the street from the entrance to the Resurrection United Methodist church. Inspection performed the day after outage but location could not be determined by the information originally given. By the time the location was confirmed, the tree had already been cleaned up. The fault also locked out the circuit, see tkt 10902537. DPAC has been notified and is investigating ~~~ 9/15/2018 ¦ AArias ¦ Investigative Action
187 | Veg - MED35 | Durham AArias | GARRETT RD - 14202411 | 9/14/2018 12:13 | 9/14/2018 13:59 | 10902535 | S-RCL - ABC Size: 800 VPTT FID: 38998805 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | PT PINE | 30 | F2 Forced Outage | 12 Hurricane | 1694 | 2890 | 106 | 4705 Old Chapel Hill Rd | CMPL 2018-09-14 14:02:00 by NZJACKS RMK: LARGE PINE TREE @ BUCHANAN DR & OLD CHAPEL HILL RD RECLOSER LOCKOUT. TARGETS B-C. FMAG 3104. ALSO LOCKED OUT CIRCUIT | aarias// MED - hurricane. Recloser locked out (tkt 10902535) due to a live pine tree that broke near the base and fell across all 3 phases from 30' away directly across the street from the entrance to the Resurrection United Methodist church. Inspection performed the day after outage but location could not be determined by the information originally given. By the time the location was confirmed, the tree had already been cleaned up. The fault may have also locked out the circuit, see tkt 10902537. DPAC has been notified and is investigating ~~~ 9/15/2018 ¦ AArias ¦ Investigative Action
188 | Veg - MED35 | Chatham County C80721 | BYNUM 230KV - BYNUM 23KV | 9/14/2018 12:27 | 9/14/2018 13:25 | 4824930 | OCB - ABC FID: T1025B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | UN Unknown Species | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 3705 | 4107 | 58 | 10L611 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON DOUBLE CIRCUIT 10L611 | aarias// Tree on double ckt, Fearrington 24KV also out. See event 4824949 ~~~ 9/19/2018 ¦ C80721 ¦ Investigative Action
189 | Veg - MED35 | Chatham County AArias | BYNUM 230KV - FEARRINGTON 24KV | 9/14/2018 12:29 | 9/14/2018 13:22 | 4824949 | OCB - ABC FID: T1025B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | UN Unknown Species | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1815 | 1897 | 53 | Node~25964587 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON DOUBLE CIRCUIT 10L611 | aarias// Tree on double ckt, Bynum 24KV also out. See event 4824930 ~~~ 9/26/2018 ¦ AArias ¦ Investigative Action
190 | Veg - MED35 | Selma omshistproc | WILSON MILLS 230KV - WILSON MILLS 24KV | 9/14/2018 12:29 | 9/15/2018 16:00 | 4829089 | RECLOSER - ABC FID: 1BLT64_113144051 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 539 | 2102 | 1651 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree tree | ... NO OUTAGE REVIEW INFO
191 | Veg - MED35 | Garner c72037 | FUQUAY 230KV - FUQUAY 23KV | 9/14/2018 12:37 | 9/15/2018 13:28 | 4832092 | OCB - B FID: T4710B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TL Tree fails, NAC | 29 Permanent Repair | 29 Conductor, bare | CR Eastern Redcedar | 6 | F2 Forced Outage | 12 Hurricane | 1353 | 2336 | 1491 |  | Missing Missing Missing span guy and #4BC down between F324BH and F325BH | MHS- live 8" in DIA. tree broke and fell into cedar tree pushing cedar tree into primary and burning down 2 of the 3 phases locking out the FCB. crew cleared tree and repaired primary than had DCC reenergize the FCB ~~~ 10/4/2018 (19 days) ¦ c72037 ¦ Investigative Action
192 | Veg - MED35 | Asheboro omshistproc | ROBBINS 115KV - ROBBINS CITY 23KV | 9/14/2018 13:03 | 9/15/2018 09:19 | 4833887 | RECLOSER - BC FID: 2089_2388107 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 763 | 1533 | 1215 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree ell tore wire down tree ell tore wire down | ... NO OUTAGE REVIEW INFO
193 | Veg - MED35 | Raleigh omshistproc | LEESVILLE WOOD VALLEY 230KV - BAILEYWICK ROAD 24KV | 9/14/2018 13:24 | 9/15/2018 10:03 | 4825788-1 | SWITCH - ABC FID: E769BL_2867546 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 826 | 1627 | 1239 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None Tree fell on power lines causing extensive damage. Power lines are down for 9 poles. Will block off Creedmoor Rd & work through the night to restore power. | ... NO OUTAGE REVIEW INFO
194 | Veg - MED35 | Sanford omshistproc | JONESBORO 230KV - BROADWAY 24KV | 9/14/2018 13:44 | 9/14/2018 14:49 | 4826038 | RECLOSER - A C FID: 17GW43_104175200 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 765 | 1163 | 65 | Load~13C700 | Tree/Vegetatn Limb Fell from Outside Right of Way None LIMB ON LINE | ... NO OUTAGE REVIEW INFO
195 | Veg - MED35 | Chapel Hill AArias | EASTGATE RET - 19021206 | 9/14/2018 13:51 | 9/14/2018 14:27 | 10902873 | S-RCL - ABC Size: 560 WVE FID: 39005400 | 02 Line Recloser | OH Distribution Line Overhead | EA Weather | 03 Tree (Vegetation) | 16 Closed Recl or Sectionalizer | NA | UN Unknown Species |  | P4 Crew Initiated Outage | 12 Hurricane | 593 | 1096 | 36 |  | steve hamlett has recloser open for tree trimming | aarias// MED - hurricane in area. RCL open for tree trimming ~~~ 9/27/2018 ¦ AArias ¦ Completion Codes or Remarks
196 | Veg - MED35 | Garner c72037 | GARNER WHITE OAK 230KV - WHITE OAK 24KV | 9/14/2018 14:00 | 9/15/2018 18:21 | 4833643 | OCB - ABC FID: T4730B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | UU Unknown Manufacturer | 5 | F2 Forced Outage | 12 Hurricane | 1878 | 1908 | 1701 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | MHS- ran FMS and CYME for fault locations. rode line out and found nothing no pics or outage review ~~~ 10/4/2018 (19 days) ¦ c72037 ¦ Investigative Action
197 | Veg - MED35 | Raleigh DFontan | METHOD 230KV - DIXIE TRAIL 12KV | 9/14/2018 14:10 | 9/14/2018 15:34 | 4826436 | OCB - ABC FID: T4990B39 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LR Tree limb, dead, overhang | D2 Dead | NA | PL Pine, loblolly | 8 | F2 Forced Outage | 12 Hurricane | 1357 | 1367 | 84 | BN50BL - BN52BL | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | Fontana 9/27/18 - 4" diameter by 15' long dead limb broke off of a 3' by 80' tall loblolly pine 8 feet off the feeder center line. The limb fell onto the feeder in between span BN50BL - BN52BL ultimately locking out the FCB. NO DAMAGE (Hurricane Florence) ~~~ 9/27/2018 ¦ DFontan ¦ Investigative Action
198 | Veg - MED35 | Selma i70604 | PRINCETON 115KV - PEEDIN JUNCTION 24KV | 9/14/2018 14:31 | 9/14/2018 19:10 | 4820579 | OCB - ABC FID: T5935B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 38 Insulator | PT PINE | 63 | F2 Forced Outage | 12 Hurricane | 1900 | 2527 | 279 | R645 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Tree fell across all 3 phases at Dis# R645 R645 tre crew needed.3612 bizzel grove ch rd , 1-ptp& insulator. | CPS// 85' pine tree located 63' from centerline fell on conductor near dis#R645 causing the circuit breaker to open and the middle phase insulator to break // Responding L&S techs repaired the insulator and removed the tree from the line with the aid of out of town crews // Equipment damaged included 367 insulator and PTP // No apparent defect on tree // Customer count was reviewed per CYME and is correct// Hurricane ~~~ 9/24/2018 ¦ i70604 ¦ Investigative Action
199 | Veg - MED35 | Raleigh DFontan | RALEIGH 115KV - SAINT MARYS STREET 12KV | 9/14/2018 14:31 | 9/14/2018 16:10 | 4826960 | OCB - ABC FID: T5160B09 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 28 Patrolled & No Problem Found | NA | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1292 | 1062 | 99 |  | Tree/Vegetatn Tree/Limb Growth None hurricane | Peel/Fontana 9/27/18 - The FCB locked out at 2:30:12 PM due to a fault which initially began as C-phase to GND then eventually involved the other phases. The responding C&M tech chose "Tree/Limb Growth: as the cause and entered "Hurricane". Engineers performed FMS-Cyme analysis to determine the fault location to be between 0W93 and CY07BL. Engineers thoroughly patrolled this line section but failed to find the actual culprit. We noticed trees in the line all along the line section and one pole LAZ96 was completely engulfed in vine & tree branches from the ground to above the top of the primary. No damage noticed. ~~~ 9/27/2018 ¦ DFontan ¦ Investigative Action
200 | Veg - MED35 | Asheboro omshistproc | TROY BURNETTE STREET 115KV - BILHEN STREET 13kV | 9/14/2018 14:32 | 9/15/2018 11:00 | 4827876 | OCB - ABC FID: T1612B11 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 524 | 524 | 1228 | Switch~T1612B11 | Tree/Vegetatn Limb Fell from Outside Right of Way None | ... NO OUTAGE REVIEW INFO
201 | Veg - MED35 | Chatham County AArias | PITTSBORO 230KV - BIG WOODS 23KV | 9/14/2018 14:38 | 9/14/2018 17:20 | 4826833-2 | SWITCH - ABC FID: 6P839_2495784 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | UN Unknown Species | 5 | F2 Forced Outage | 12 Hurricane | 1036 | 1427 | 162 | Node~1082375 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE TORN DOWN LINE AT CQ36AF | aarias// MED - hurricane in area. Tree tore down line at CQ36AF. Recommend installing fuse at DIS 6RP70 ~~~ 9/26/2018 ¦ AArias ¦ Investigative Action
202 | Veg - MED35 | Sanford omshistproc | BEAR BRANCH 230KV - BENHAVEN 24KV | 9/14/2018 14:46 | 9/14/2018 18:29 | 4828320 | RECLOSER - ABC FID: K569AC_112233684 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 505 | 1566 | 223 | Node~1057431 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE FELL ON LINE tap at k713ac--single phse down | ... NO OUTAGE REVIEW INFO
203 | Veg - MED35 | Asheboro omshistproc | RAMSEUR 115KV - FRANKLINVILLE 24KV | 9/14/2018 14:46 | 9/14/2018 16:21 | 4826990 | RECLOSER - ABC FID: 17TG07_104444878 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1067 | 1996 | 95 | Recloser~17TG07_104444878 | Tree/Vegetatn Limb Fell from Outside Right of Way None | ... NO OUTAGE REVIEW INFO
204 | Veg - MED35 | Sanford omshistproc | SANFORD HORNER BLVD. 230KV - GULF 23KV | 9/14/2018 14:50 | 9/14/2018 17:15 | 4828608 | RECLOSER - ABC FID: T675AC_2361168 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 534 | 1839 | 144 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None limb fell into primary limb fell into primary | ... NO OUTAGE REVIEW INFO
205 | Veg - MED35 | Garner omshistproc | MILBURNIE 230KV - BELTLINE 23KV | 9/14/2018 15:15 | 9/14/2018 15:40 | 4827538 | RECLOSER - ABC FID: GT69BJ_104342196 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 3981 | 1100 | 25 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None | ... NO OUTAGE REVIEW INFO
206 | Veg - MED35 | Raleigh DFontan | RALEIGH YONKERS ROAD 115KV - CRABTREE CREEK 24KV | 9/14/2018 15:35 | 9/14/2018 19:35 | 4827678 | RECLOSER - BC FID: 0C08BK_104336296 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | NA | OW Oak, willow | 30 | F2 Forced Outage | 12 Hurricane | 1212 | 2151 | 240 | RDS38-RDS36 | Tree/Vegetatn Limb Fell from Outside Right of Way None limb on line limb on line | Peel/Fontana 9/27/18 - 1" diameter by 5' long live limb fell from a 3' diameter by 60' tall willow oak tree 13' off of the line CL, and laid on the primary conductors in span RDS38-RDS36, locking out B & C phases of the recloser. NO DAMAGE (hurricane Florence) ~~~ 9/27/2018 ¦ DFontan ¦ Investigative Action
207 | Veg - MED35 | Chatham County AArias | SILER CITY 115KV - ROCKY RIVER 24KV | 9/14/2018 16:30 | 9/14/2018 17:10 | 4828492 | OCB - ABC FID: T1530B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | UN Unknown Species | 5 | F2 Forced Outage | 12 Hurricane | 1618 | 1689 | 40 | Node~1284222 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree in line at 2415AF tree in line at 2415AF | aarias// MED - hurricane in area. Tree inside R/W @ 2415AF ~~~ 9/26/2018 ¦ AArias ¦ Investigative Action
208 | Veg - MED35 | Garner c72037 | HOLLY SPRINGS 230KV - RHAMKATTE 24KV | 9/14/2018 16:46 | 9/15/2018 11:05 | 4828656 | OCB - ABC FID: T4795B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | 29 Permanent Repair | 29 Conductor, bare | PT PINE | 15 | F2 Forced Outage | 12 Hurricane | 1443 | 1526 | 1099 | C123BH | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree on line at c123bh tree on line at c123bh | MHS- Dead pine tree about 8" in DIA. fell from ground level and 15' from C/L, falling across all 3 phases burning down 2 of the 3 phases. locking out the FCB. Crew climbed poles and did a permanent repair. Than had DCC reenergize the FCB ~~~ 10/4/2018 (19 days) ¦ c72037 ¦ Investigative Action
209 | Veg - MED35 | Garner c72037 | HOLLY SPRINGS 230KV - BRACKENRIDGE 24KV | 9/14/2018 16:49 | 9/15/2018 20:35 | 4828881 | SWITCH - ABC FID: C110BH_112165274 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | UU Unknown Manufacturer | 5 | F2 Forced Outage | 12 Hurricane | 579 | 1824 | 1666 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree on feeder tree on feeder | MHS- no fault location ran FMS and CYME rode out locations found nothing. no pics or outage review ~~~ 10/4/2018 (19 days) ¦ c72037 ¦ Investigative Action
210 | Veg - MED35 | Raleigh e68825 | RALEIGH HONEYCUTT 230KV - HONEYCUTT 24KV | 9/14/2018 17:10 | 9/14/2018 21:19 | 4833734-2 | OCB - ABC FID: T5123B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | PV Pine, Virginia | 10 | F2 Forced Outage | 12 Hurricane | 1,798 Cust Eq: 1167 | 1829 | 249 | WM94BK-JM58BK | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE | Peel/Fontana 9/26/18: A 6" diam. x ~ 60' tall Virginia Pine 10' off of the line CL, broke at 35' above the GL, fell into the feeder in span WM94BK-JM58BK, and locked out the FCB. No Damage. PEEL 11/16/18: The Self-Healing Team â€œTieâ€ recloser GA15BL closed at 19:00, picking up load on the Honeycutt feeder back to recloser D095BK (1167 customers saved). Crews removed the tree from the line, then had DCC close the FCB at 21:19 to restore service to the feeder. ~~~ 9/26/2018 ¦ e68825 ¦ Investigative Action
211 | Veg - MED35 | Henderson omshistproc | OXFORD NORTH 230KV - OXFORD EAST 23KV | 9/14/2018 17:21 | 9/14/2018 18:06 | 4829255-1 | OCB - ABC FID: T5090B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 966 | 1019 | 45 | Fuse~ETU34_1224366 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree fell on the line tearing down primary at ETU36 tree fell on the line tearing down primary at ETU36 | ... NO OUTAGE REVIEW INFO
212 | Veg - MED35 | Sanford omshistproc | SANFORD HORNER BLVD. 230KV - GULF 23KV | 9/14/2018 17:21 | 9/16/2018 10:30 | 4832482 | RECLOSER - ABC FID: T675AC_2361168 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 551 | 1839 | 2469 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE TREE | ... NO OUTAGE REVIEW INFO
213 | Veg - MED35 | Asheboro omshistproc | BISCOE 115KV - HIGHWAY 220 23KV | 9/14/2018 17:22 | 9/15/2018 12:28 | 4833676 | RECLOSER - ABC FID: 8872_108208074 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 570 | 898 | 1146 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Two trees fell on primary. Two trees fell on primary. | ... NO OUTAGE REVIEW INFO
214 | Veg - MED35 | Cary c72037 | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 9/14/2018 17:23 | 9/14/2018 21:55 | 4832136 | RECLOSER - AB FID: 5DF10_112849190 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | UU Unknown Manufacturer | 5 | F2 Forced Outage | 12 Hurricane | 1746 | 2825 | 272 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree | MHS- no fault location given, ran FMS and CYME rode out location and found nothing no pics or outage review ~~~ 10/4/2018 (20 days) ¦ c72037 ¦ Investigative Action
215 | Veg - MED35 | Chatham County AArias | PITTSBORO 230KV - BIG WOODS 23KV | 9/14/2018 17:43 | 9/14/2018 18:38 | 4831789 | OCB - ABC FID: T2250B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | UN Unknown Species | 5 | F2 Forced Outage | 12 Hurricane | 1401 | 1427 | 55 | Node~1082351 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON PRIMARY AT CS55AF | aarias// MED - hurricane in area. Tree on primary at CS55AF ~~~ 9/26/2018 ¦ AArias ¦ Investigative Action
216 | Veg - MED35 | Sanford omshistproc | JONESBORO 230KV - OLIVIA 24KV | 9/14/2018 17:56 | 9/15/2018 14:41 | 4834318 | OCB - ABC FID: T2141B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 831 | 846 | 1246 | Line~8843AC_8844AC_2442408 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None LINE DOWN 911 12505910 OPENED UP SB 6BQ81 | ... NO OUTAGE REVIEW INFO
217 | Veg - MED35 | Selma omshistproc | SELMA 230KV - MICRO 23KV | 9/14/2018 19:19 | 9/14/2018 21:12 | 4834581 | RECLOSER - ABC FID: 11Q013_104210001 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 03 Wind | 1173 | 2064 | 113 | Recloser~11Q013_104210001 | Tree/Vegetatn Tree/Limb Growth None TREES | ... NO OUTAGE REVIEW INFO
218 | Veg - MED35 | Sanford i25781 | SANFORD GARDEN STREET - FIRETOWER ROAD 23KV | 9/14/2018 19:27 | 9/14/2018 23:36 | 4834118 | OCB - ABC FID: T2432B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TL Tree fails, NAC | DN No apparent defect | NA | OA Oak | 19 | F2 Forced Outage | 17 Wind and Rain | 1190 | 1194 | 249 | 2704AC | Missing Missing Missing | JWW// On 9/14/18 at 19:27 during hurricane Florence an oak tree fell from outside of the right of way across all three phases at 2704AC locking out the FCB and causing 1190 customers to lose power. When the Tech arrived he cut tree off of the three phase and had DCC energize the FCB at 23:36 restoring power to all customers. No damage was done to conductor. ~~~ 9/27/2018 ¦ i25781 ¦ Investigative Action
219 | Veg - MED35 | Asheboro omshistproc | ROBBINS 115KV - ROBBINS CITY 23KV | 9/14/2018 19:50 | 9/16/2018 08:30 | 4840175 | RECLOSER - A C FID: 2089_2388107 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 749 | 1533 | 2200 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell on feeder tree fell on feeder | ... NO OUTAGE REVIEW INFO
220 | Veg - MED35 | Durham rlw2159 | GREEN STREET - 14121210 | 9/14/2018 20:00 | 9/14/2018 22:15 | 10904680 | SOH - ABC Size: 600 Line Disconnect FID: 39035690 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LH Tree limb, overhang | DN No apparent defect | 29 Conductor, bare | OW Oak, willow | 0 | F2 Forced Outage | 12 Hurricane | 1469 | 1889 | 135 | aarias// W Club Blvd, 1 span East of Oakland Ave | CMPL 2018-09-14 22:30:00 by MCLANDE RMK: LOCK OUT...TARGETS ABG & FMAG 4149. PRIMARY DOWN NEAR THE CORER OF OAKLAND & WEST CLUB | aarias// med day hurricane Florence.... Overhang willow oak limbs fell and took down 3 phases of one span of primary. Primary repaired. No follow up needed ~~~ 9/14/2018 ¦ rlw2159 ¦ Investigative Action
221 | Veg - MED35 | Raleigh DFontan | RALEIGH TIMBERLAKE 115KV - BRENTWOOD 23KV | 9/14/2018 20:10 | 9/14/2018 21:22 | 4835271 | SWITCH - ABC FID: K27BK_1204923 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | NA | AS Ash | 10 | P4 Crew Initiated Outage | 12 Hurricane | 1337 | 2195 | 72 | AG73BK | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE AG73BK | Peel/Fontana 9/27/18: A 4" dia. x 20' long dead limb form a 2' dia. x ~ 60' tall Ash menacing the feeder at AG73BK, leaned into the feeder and was contacting the phase conductors, causing the FCB to relay numerous times between 3:50 PM and 8:08 PM. The responding crew opened ABS K27BK at ~8:10 PM to allow the tree crew to safely cut & remove the limb from the line. ~~~ 9/27/2018 ¦ DFontan ¦ Investigative Action
222 | Veg - MED35 | Chapel Hill AArias | HILLSBOROUGH - 19081202 | 9/14/2018 21:56 | 9/14/2018 22:32 | 10904965 | SolidBar - ABC Size: 300 Solid Bar FID: 39041276 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DC Internal stem decay | P1 Pole, Creosote | OA Oak | 55 | P4 Crew Initiated Outage | 12 Hurricane | 580 | 1457 | 36 | aarias// 408 Calvin St | LOCK OUT, POSSIBLE FAULT LOCATION BACK LINE DOUBLE CIRCUIT BETWEEN CALVIN ST AND THE STATION EXIT. | aarias// MED - hurricane in area. Diseased oak tree (largest tree in the town of Hillsborough) fell from 55 ft away across the street in front of 408 Calvin St on double pole line for Hillsborough 1201 (tkt 109039122) and Hillsborough 1202 (tkt 109039121). Visual inspection of tree revealed internal stem decay. Damaged 2 45' poles, 1 30' pole, primary wire on both circuits, and several crossarms across 6 spans of primary. Jumpers were cut and a set of Solid Blades (FACID 39041276) was closed to isolate damage and backfeed most of 1201 from 1202. Solid blades and 1202 breaker (tkts 10904965 & 10904904) open to restore feed to normal. ~~~ 9/14/2018 ¦ AArias ¦ Investigative Action
223 | Veg - MED35 | Chapel Hill AArias | HILLSBOROUGH - 19081202 | 9/14/2018 21:56 | 9/14/2018 22:31 | 10904904 | S-CKT - ABC Size: Class 1 FID: 38359317 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | TF Tree fails, defective | 14 Closed Breaker | P1 Pole, Creosote | OA Oak | 55 | P4 Crew Initiated Outage | 12 Hurricane | 988 | 1457 | 35 | PRIMARY DOWN AT REX DRIVE | OPENED BREAKER TO RETURN CIRCUIT BACK TO NORMAL FROM WHERE PART OF IT WAS BACK FED FROM HILLSBOROUGH 1201. CAUSE WAS PRIMARY DOWN AT REX DRIVE. KEVIN SHAMBLEY/919-201-4358 | aarias// MED - hurricane in area. Diseased oak tree (largest tree in the town of Hillsborough) fell from 55 ft away across the street in front of 408 Calvin St on double pole line for Hillsborough 1201 (tkt 109039122) and Hillsborough 1202 (tkt 109039121). Visual inspection of tree revealed internal stem decay. Damaged 2 45' poles, 1 30' pole, primary wire on both circuits, and several crossarms across 6 spans of primary. Jumpers were cut and a set of Solid Blades (FACID 39041276) was closed to isolate damage and backfeed most of 1201 from 1202. Solid blades and 1202 breaker (tkts 10904965 & 10904904) open to restore feed to normal. ~~~ 9/14/2018 ¦ AArias ¦ Investigative Action
224 | Veg - MED35 | Sanford i25781 | SANFORD GARDEN STREET - SOUTH HORNER 23KV | 9/14/2018 22:06 | 9/15/2018 10:21 | 4835897 | OCB - ABC FID: T2432B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 24 N/A | NA | UN Unknown Species |  | F2 Forced Outage | 17 Wind and Rain | 1584 | 1585 | 735 | Line~T008AC_T009AC_2437281 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE ON LINE | JWW// On 9/14/18 at 22:06 during hurricane Florence a limb fell on the tree phase at T008AC causing the South Horner Blvd FDR to lock out and 1584 customers to lose power. When the tech arrived he got the limb off and had DCC energize the feeder on 9/15/18 at 10:21. I searched for the limb but could not find it. No damage was done to the conductor. ~~~ 9/27/2018 ¦ i25781 ¦ Investigative Action
225 | Veg - MED | Sanford i25781 | BEAR BRANCH 230KV - SEMINOLE 24KV | 9/15/2018 01:32 | 9/15/2018 09:23 | 4836506 | OCB - ABC FID: T2443B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 24 N/A | NA | UN Unknown Species |  | F2 Forced Outage | 17 Wind and Rain | 1346 | 1371 | 471 | Load~H482AC | Tree/Vegetatn Limb Fell from Inside Right of Way None LIMB ON LINE 911 TICKET 12494458 | JWW// On 9/15/18 at 01:32 during hurricane Florence a small limb fell on the three phase locking out the Seminole feeder causing 1346 customers to lose power. When the service tech arrived he knocked the limb off with a stick and had DCC energize the feeder restoring power to all 1346 customers. When I went to investigate I could not find the limb. ~~~ 9/26/2018 ¦ i25781 ¦ Investigative Action
226 | Veg - MED | Asheboro i25781 | ASHEBORO NORTH 115KV - WORTHVILLE 24KV | 9/15/2018 06:10 | 9/15/2018 07:42 | 4837117 | OCB - ABC FID: T0965B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 17 | F2 Forced Outage | 12 Hurricane | 1397 | 1411 | 92 | H008AD | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell on 3 phase lines @ H008AD. tree fell on 3 phase lines @ H008AD. | JWW// On 9/15/18 at 06:10am during hurricane Florence a dead pine tree fell across all 3 phases at H008AD causing the Worthville FDR to lockout resulting in 1397 customers to lose power. When the service tech arrived he cut small dead pine tree off of the 3 phase and had DCC energize the FDR at 07:42am restoring power to all 1397 customers. No damage was done to the conductor. ~~~ 9/19/2018 ¦ i25781 ¦ Investigative Action
227 | Veg - MED | Sanford i25781 | SANFORD GARDEN STREET - CARTHAGE STREET 23KV | 9/15/2018 17:49 | 9/15/2018 20:21 | 4834128 | SWITCH - ABC FID: 0016AC_2450569 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | PT PINE | 21 | P4 Crew Initiated Outage | 17 Wind and Rain | 2234 | 2305 | 152 | 1385AC | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None DROPPED TO PULL UP LINE TO ENERGIZED DOUBLE CIRCUIT | JWW// On 9/15/18 at 17:49 during hurricane Florence a large pine tree fell at 1385AC tearing down the three phase on the hospital feeder. When the crew arrived they felt the only safe way to get the primary back up was to drop the Carthage Street FDR so they could pull the primary back up on the double circuit pole. When the crew finished their work they had DCC energize the FDR at 20:21. ~~~ 9/26/2018 ¦ i25781 ¦ Investigative Action
228 | Veg - MED | Garner c72037 | FUQUAY 230KV - FUQUAY SOUTH PARK 23KV | 9/15/2018 19:24 | 9/15/2018 19:42 | 4841647 | OCB - ABC FID: T4710B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | UU Unknown Manufacturer | 30 | F2 Forced Outage | 12 Hurricane | 2971 | 3385 | 18 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE ON LINE | MHS- Ran FMS and CYME . rode out locations and found nothing no pics, or outage review ~~~ 10/4/2018 (19 days) ¦ c72037 ¦ Investigative Action
229 | Veg - MED | Garner c72037 | FUQUAY 230KV - FUQUAY 23KV | 9/15/2018 21:00 | 9/16/2018 09:59 | 4842622-1 | RECLOSER - BC FID: 17ET32_104160155 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin | NA | UU Unknown Manufacturer | 5 | F2 Forced Outage | 12 Hurricane | 1767 | 2336 | 779 | Load~G279BH | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | MHS- rode out this location found nothing yard cleaned up no pics, or outage reports ~~~ 10/4/2018 (18 days) ¦ c72037 ¦ Investigative Action
230 | Veg - MED | Chapel Hill AArias | EASTGATE RET - 19021205 | 9/15/2018 22:54 | 9/16/2018 00:46 | 10909809 | S-CKT - ABC Size: Class 3 FID: 38358945 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 26 Vines | 14 Closed Breaker | NA | KZ Kudzu | 0 | F2 Forced Outage | 12 Hurricane | 1009 | 1010 | 112 | intersection of tadley dr and markham dr | CMPL 2018-09-16 00:48:00 by LEMCKIN RMK: locked out with targets 50 a to c and fmag 3784...DMS shows fault halo on Markham Dr...RODE OUT AND FOUND VINES ON POLE AT MARKHAM | aarias// MED - hurricane in area. Vines on pole at Markham Dr, vines removed. Long duration outage project in place to relocate pole line from Markham Dr to Tadley Dr, see WO 27644064 ~~~ 9/17/2018 ¦ AArias ¦ Investigative Action
231 | Veg - MED | Chapel Hill AArias | WHITE CROSS - 19051202 | 9/16/2018 05:27 | 9/16/2018 06:21 | 10910991 | S-CKT - ABC Size: Class 3 FID: 38358285 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | NA | OA Oak |  | F2 Forced Outage | 12 Hurricane | 983 | 983 | 54 | aarias// near NC 54 & Butler Rd | locked out with targets 51 a,b,c and fmag 2356 | aarias// MED - hurricane in area. Per Matt Williams at DCC, small dead oak limb across all phases, could not determine point of origin. Location not provided to DCC, FMAG puts location near NC 54 and Butler Rd. Limb removed and ckt energized ~~~ 9/18/2018 ¦ AArias ¦ Completion Codes or Remarks
232 | Veg - MED | Durham AArias | GARRETT RD - 14202413 | 9/16/2018 08:21 | 9/16/2018 14:16 | 10911867 | FOH - ABC Size: 125 SMU-20 (E) FID: 38863486 | 03 Line Fuse | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 830 | 5339 | 355 | high gate at fox chase apt. back property | CMPL 2018-09-16 14:16:00 by JAU4299 RMK: MULITPLE OUT UNDER 125 SMU... LIVE TREE IN THE R/W. JOHNNYU. BACK PROPERTY | aarias// LIVE TREE IN THE R/W. JOHNNYU. BACK PROPERTY. No field investigation performed ~~~ 9/18/2018 ¦ AArias ¦ Completion Codes or Remarks
233 | Veg - MED | Durham AArias | POPE ROAD - 14082403 | 9/16/2018 21:11 | 9/17/2018 17:18 | 10930053 | SOH - ABC Size: 600 Line Disconnect FID: 39034596 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DE Erosion/poor enviornment | PP Pole | PT PINE | 65 | P4 Crew Initiated Outage | 12 Hurricane | 2538 | 3214 | 1207 |  | BROKEN 40/5, 8' XARM, 25KV SWITCH, 3INSULATORS, 2 BRACES, #2. AT CORNER OF ERWIN RD & PICKETT RD. RECLOSER 410944391 & SOLIDS 39034596 OPENED TO ISOLATE FAULT. SHT 074 DID NOT OPERATE. CLOSED OPEN POINT 398668029 TO BACK FEED. SEE ADDT INFO ABOUT GROUND | aarias// MED - hurricane in area. Large live pine tree uprooted and fell from 65 ft away across Erwin Rd directly on top of corner pole at Erwin Rd and Pickett Rd. Broke pole, crossarm, and tap fuse. Tore down primary across Pickett Rd. SHT 74 didn't operate, crews isolated damage by opening Solid Blades FACID 39034596 (tkt 10930053) and Recloser FACID 410944391. Repairs delayed due to inclement weather conditions. Closed open point Recloser FACID 398668029 to backfeed from Pope Rd 2410. Recloser 404662272 opened (tkt 10920399) to close Solid Bars and restore the feed once repairs were complete. ~~~ 9/21/2018 ¦ AArias ¦ Investigative Action
234 | Veg - MED | Durham AArias | ENO - 14102401 | 9/17/2018 07:42 | 9/17/2018 17:46 | 10917786 | S-CKT - ABC Size: Class EX FID: 38355777 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 42 Recloser, Hydraulic | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 938 | 938 | 604 | aarias// Cornwallis Rd & Murphy School Rd | RCL outage. CIRCUIT OPENED TO CLOSE IN RECLOSER 38998791... 140E RCL NEEDS TO BE CHANGED OUT... BOBBY TAP IS AWARE PER CHARLES MCCARTHY | aarias// MED - hurricane in area. Tree pulled down lines at Cornwallis Rd & Murphy School Rd. Upstream recloser damaged, to be changed out under WO 26711293. No field investigation ~~~ 9/20/2018 ¦ AArias ¦ Work Order(s) Generated
235 | Veg - MED | Roxboro i67431 | BAHAMA 230KV - ROUGEMONT 23KV | 9/17/2018 09:56 | 9/17/2018 11:01 | 4851217-2 | RECLOSER - ABC FID: E0C13_104887891 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | PT PINE | 40 | F2 Forced Outage | 02 Rain | 1172 | 1906 | 65 | EZM58 | Overhead Fac Overhead Connections / Jumper Failure Jumper Burned In Two | DPW: Dead Pine tree fell at EZM58, breaking conductors and locking out the OCB. Switch EZM66 was opened and Recloser E0C13 was closed in to tie in the Durham Road Feeder as a back feed. Repairs were made to the conductor (spliced) ~~~ 9/19/2018 ¦ i67431 ¦ Investigative Action
236 | Veg - MED | Roxboro i67431 | BAHAMA 230KV - ROUGEMONT 23KV | 9/17/2018 09:56 | 9/17/2018 10:50 | 4851217-1 | OCB - ABC FID: T4555B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | PT PINE | 40 | F2 Forced Outage | 02 Rain | 601 | 1906 | 54 | Load~5276K | Overhead Fac Overhead Connections / Jumper Failure Jumper Burned In Two | DPW: Dead Pine tree fell at EZM58, breaking conductors and locking out the OCB. Switch EZM66 was opened and Recloser E0C13 was closed in to tie in the Durham Road Feeder as a back feed. Repairs were made to the conductor (spliced) ~~~ 9/19/2018 ¦ i67431 ¦ Investigative Action
237 | Veg - MED | Durham AArias | POPE ROAD - 14082403 | 9/17/2018 15:04 | 9/17/2018 17:36 | 10919875 | S-RCL - ABC Size: 800 VPTT FID: 410935830 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | TL Tree fails, NAC | DN No apparent defect | PP Pole | PT PINE | 50 | P4 Crew Initiated Outage | 12 Hurricane | 819 | 3214 | 152 | aarias// Erwin Rd at Pickett Rd | DCC opened RCL due to loading issues. frequent power interruptions - lasting hours at a time.... | aarias// part of larger outage involving SH team 74. Ckt 2403 backfed from 2410 up to RCL S/o Randolph on Erwin Rd. RCL 5830 had to be dropped due to excessive load on 150E FACID 169548590. It was later discovered that the 150Es were swapped for solid blades in the field, but GIS was never updated. See tkt 10853903 ~~~ 9/20/2018 ¦ AArias ¦ Investigative Action
238 | Veg - MED | Zebulon i70604 | KNIGHTDALE 115KV - KNIGHTDALE WEST 24KV | 9/18/2018 12:25 | 9/18/2018 13:25 | 4857223 | OCB - ABC FID: T4850B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LL Tree limb fails | DN No apparent defect | NA | PT PINE |  | F2 Forced Outage | 12 Hurricane | 1945 | 1971 | 60 | F260BF | Missing Missing Missing | CPS// Pine limb fell from outside of R/W making contact with conductor at dis#F260BF causing circuit breaker to open // limb was cleared and circuit was re-energized// Wind was blowing moderately and limb may have been hanging left over from Hurricane // No damage to equipment // No apparent defect on limb ~~~ 9/24/2018 ¦ i70604 ¦ Investigative Action
239 | Veg - MED | Garner c72037 | RALEIGH WORTHDALE 230KV - GLENBROOK 23KV | 9/19/2018 10:16 | 9/19/2018 11:36 | 4860516 | OCB - ABC FID: T5168B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 6 | F2 Forced Outage | 00 Calm | 1614 | 1608 | 80 | AH34BJ | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | MHS- A dead pine tree limb about 8" in DIA. and approx. 45' up in the air and 6' from C/L broke out of tree falling across all 3 phases locking out the FCB. crew cleared limb and had DCC reenergize the FCB back up ~~~ 10/4/2018 (15 days) ¦ c72037 ¦ Investigative Action
240 | Veg - MED | Garner c72037 | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 9/19/2018 17:20 | 9/19/2018 20:30 | 4862670-1 | RECLOSER - A FID: G0P96_104694169 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | DN No apparent defect | NA | MP Maple |  | F2 Forced Outage | 00 Calm | 646 | 2861 | 190 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None opened all 3 single phase reclosures and trimmed trees opened all 3 single phase reclosures and trimmed trees | MHS-crew found Maple tree growing up into primary at DIS FA21BJ, locking out A phase on recloser at G0P96. crew had DCC open up BC phase so that they could cut back limbs , they then had DCC reenergize recloser at G0P96 ~~~ 10/4/2018 (15 days) ¦ c72037 ¦ Investigative Action
241 | Veg - MED | Garner c72037 | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 9/19/2018 19:56 | 9/19/2018 20:30 | 4863016 | RECLOSER - BC FID: G0P96_104694169 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin | NA | MP Maple | 0 | P4 Crew Initiated Outage | 00 Calm | 1135 | 2861 | 34 | FA21BJ | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree on line between fa21bj and fa22bj. opened all 3 single phase reclosures and trimmed trees | MHS-crew found Maple tree growing up into primary at DIS FA21BJ, locking out A phase on recloser at G0P96. crew had DCC open up BC phase so that they could cut back limbs , they then had DCC reenergize recloser at G0P96 ~~~ 10/4/2018 (15 days) ¦ c72037 ¦ Investigative Action
242 | Veg | Henderson i67431 | OXFORD SOUTH 230KV - STEM 23KV | 9/23/2018 00:55 | 9/23/2018 02:58 | 4868802-1 | SWITCH - ABC FID: EVY91_2763394 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  | OA Oak | 25 | F2 Forced Outage | 02 Rain | 591 | 2535 | 123 | Open Bridge~Line Cut-610559 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Live oak tree fell from outside right of way at ES790.. Need 110' bucket from Asplundh, also need someone to move excavator t Live oak tree fell from outside right of way at ES790.. Need 110' bucket from Asplundh, also need someone to move excavator to access. | DPW: Verified coding ~~~ 9/27/2018 ¦ i67431 ¦ Completion Codes or Remarks
243 | Veg | Garner c72037 | RALEIGH WORTHDALE 230KV - GLENBROOK 23KV | 9/28/2018 04:25 | 9/28/2018 04:46 | 4872620 | SWITCH - ABC FID: RFT79_1222874 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin | NA | OA Oak | 0 | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 583 | 1608 | 21 | NA268 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | MHS- A Oak tree grew up into primary and was burning at DIS# NA268 crew opened up switch RFT79 while they cleared the tree limbs. after the limbs were cleared the closed back in switch RFT79 ~~~ 10/4/2018 ¦ c72037 ¦ Investigative Action
244 | Veg | Henderson i67431 | WARRENTON 115KV - HIGHWAY 401 NORTH 23KV | 10/4/2018 09:57 | 10/4/2018 11:04 | 4875355-2 | RECLOSER - ABC FID: EAU47_1878163 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | UU Unknown Manufacturer | 10 | F2 Forced Outage | 00 Calm | 875 | 1697 | 67 | Line~FAB87_FAB88_1859347 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE AT FAB88 | DPW: Contractor was clearing ROW for City of Warrenton Sewer project. Excavator hung vine that pulled dead tree onto the conductor causing the feeder to lock out. Crew attempt to sectionalize by opening recloser EAU47, the breaker was closed back in but did not hold. It was then that the location of the fault was identified. Solid blade EAY56 was opened, breaker closed back in(parial restoration) Fault was removed. No damage to our facilities. Feed was returned to normal. ~~~ 10/4/2018 ¦ i67431 ¦ Completion Codes or Remarks
245 | Veg | Henderson i67431 | WARRENTON 115KV - HIGHWAY 401 NORTH 23KV | 10/4/2018 09:57 | 10/4/2018 11:03 | 4875355-1 | OCB - ABC FID: T5360B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | UU Unknown Manufacturer | 10 | F2 Forced Outage | 00 Calm | 660 | 1697 | 66 | Line~FAB87_FAB88_1859347 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE AT FAB88 | DPW: Contractor was clearing ROW for City of Warrenton Sewer project. Excavator hung vine that pulled dead tree onto the conductor causing the feeder to lock out. Crew attempt to sectionalize by opening recloser EAU47, the breaker was closed back in but did not hold. It was then that the location of the fault was identified. Solid blade EAY56 was opened, breaker closed back in(parial restoration) Fault was removed. No damage to our facilities. Feed was returned to normal. ~~~ 10/4/2018 ¦ i67431 ¦ Investigative Action
246 | Veg | Henderson i67431 | OXFORD NORTH 230KV - OXFORD EAST 23KV | 10/7/2018 00:10 | 10/7/2018 00:50 | 4876172-1 | RECLOSER - ABC FID: 100565_105933562 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DD Co-dominate stem | M4 Metering CT | PP Yellow Poplar (tulip) | 18 | F2 Forced Outage | 00 Calm | 1455 | 1019 | 40 | ETU19 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Live poplar tree fell from outside right of way at ETU19 on all 3 phases causing the breaker to open Live poplar tree fell from outside right of way at ETU19 on all 3 phases causing the breaker to open | DPW: Poplar tree, diseased co-dominant stem fell at ETU19 on all three phases locking out the OCB. However, FMS does not show the breaker locking out, according to DCC and the Service Tech, it did lock out. ABS ETU32 was opened up by Service Tech, G&W recloser 100565 closed by DCC, tying in the Pinetree feeder (labeled a SHN). This isolated the fault location. Tree was cut,removed and feed was put back to normal. No damage to conductor or facilities. Outage# 4876172 â€“ On 10/7/18 the Oxford East 23KV Feeder out of the Oxford North Substation locked out at 12:10am affecting 1,664 customers. The outage was caused by a tree that fell from outside the right of way at GIS# ETU19 on all 3 phases. Switching was performed and at 12:50am 1,455 customers were restored for a duration of 40 minutes. At 2:06am another 207 customers were restored for a duration of 115 minutes. The remaining 2 customers were restored at 2:09am for a duration of 119 minutes. Total CMI was 82,554. ~~~ 10/8/2018 ¦ i67431 ¦ Investigative Action
247 | Veg - MED35 | Durham rlw2159 | OXFORD ROAD - 14091211 | 10/11/2018 08:48 | 10/11/2018 09:21 | 10943513 | SOH - ABC Size: 600 Line Disconnect FID: 39034600 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | TL Tree fails, NAC | DN No apparent defect | 74 Wire, copper | UN Unknown Species |  | P4 Crew Initiated Outage | 12 Hurricane | 677 | 1810 | 33 | 1007 N GUTHRIE | RELATED TO BROKE POLE - EV10942535 | aarias// med day hurricane Michael....circuit out see 10956709 1 phase primary down in front of 1007 N Guthrie Ave tree on power line. Opened 3 80Ts (37 cust) see 10961916 at Holloway and N Guthrie to clear. Closed solid blades see 10943513 at feeder tied to backfeed from Oxford 1211 see 109425351 ~~~ 10/18/2018 ¦ rlw2159 ¦ Completion Codes or Remarks
248 | Veg - MED35 | Garner omshistproc | ANGIER 230KV - CHALYBEATE 23KV | 10/11/2018 12:04 | 10/11/2018 12:42 | 4879805-1 | RECLOSER - ABC FID: N887BH_108855705 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 00 Calm | 772 | 1930 | 38 | Node~889387 | Tree/Vegetatn Tree/Limb Growth None TREE ON LINE AT R385BH | ... NO OUTAGE REVIEW INFO
249 | Veg - MED35 | Sanford omshistproc | SANFORD GARDEN STREET - SANFORD GARDEN STREET HOSPITAL 23KV | 10/11/2018 12:32 | 10/11/2018 13:35 | 4880125 | RECLOSER - BC FID: 108C21_104046049 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 557 | 1762 | 63 | Line~V669AC_V671AC_2436105 | Tree/Vegetatn Limb Fell from Inside Right of Way None power restored | ... NO OUTAGE REVIEW INFO
250 | Veg - MED35 | Durham AArias | RESEARCH TRIANGLE RET - 14052402 | 10/11/2018 13:08 | 10/11/2018 15:03 | 10946343 | S-RCL - ABC Size: 560 WVE FID: 39006985 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | 37 Removed Limb or Tree From Lin | 29 Conductor, bare |  |  | F2 Forced Outage | 12 Hurricane | 626 | 2562 | 115 | tree on line behind 10 ainsworth ct | CMPL 2018-10-11 15:09:00 by BJACOBY RMK: RECLOSER LOCKED OUT - TREE ON LINE AT 10 AINSWORTH CT | aarias// hurricane in area. Tree on line behind 10 Ainsworth Ct ~~~ 10/19/2018 ¦ AArias ¦ Completion Codes or Remarks
251 | Veg - MED35 | Chapel Hill AArias | HOMESTEAD - 19061208 | 10/11/2018 13:31 | 10/11/2018 15:47 | 10946966 | S-CKT - ABC Size: Class 2 FID: 38358777 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TL Tree fails, NAC | DN No apparent defect | NA | PT PINE |  | F2 Forced Outage | 12 Hurricane | 1316 | 1322 | 136 | back prop off eubanks to old 86 | CMPL 2018-10-11 15:50:00 by MWL0292 RMK: REMOVED PINE TREE OFF OF A B C PHASES LOCATED AT EUBANKS AND DROMOLAND RD | aarias// MED - hurricane Michael. Removed pine tree off all phases. No field investigation performed ~~~ 10/16/2018 ¦ AArias ¦ Completion Codes or Remarks
252 | Veg - MED35 | Raleigh DFontan | RALEIGH NORTHSIDE 115KV - AYCOCK STREET 12KV | 10/11/2018 13:40 | 10/11/2018 14:42 | 4880563 | OCB - ABC FID: T5131B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | OW Oak, willow |  | F2 Forced Outage | 02 Rain | 847 | 866 | 62 | RE102-RE109 | Tree/Vegetatn Limb Fell from Inside Right of Way None limb at re176 took out the breaker | Peel/Fontana 10/18/18: A limb from a 6' dia. x ~80' tall willow oak, 38' off of the line CL, broke off and landed on the feeder in span RE102-RE109, causing a A_B phase-phase fault, locking out the FCB. Resident customer reported hearing a loud boom (the fault) in this location, which matched up with the engineer's FMS/Cyme fault analysis' predicted fault location. No damage. Responding crew removed the limb from the line, and had DCC remotely close the FCB at 2:22 PM to restore service to the feeder. We could not determine exactly from where on the tree the limb came, nor could we determine the limb's size, as the limbs had all been collected for disposal by the residents. ~~~ 10/18/2018 ¦ DFontan ¦ Investigative Action
253 | Veg - MED35 | Zebulon | ZEBULON 115KV - PILOT 23KV | 10/11/2018 14:01 | 10/11/2018 15:34 | 4880695-2 | RECLOSER - ABC FID: BF48BF_104161628 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 567 | 1845 | 93 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None removed tree from line at BF84BF and re-energized reclosure | ... NO OUTAGE REVIEW INFO
254 | Veg - MED35 | Sanford omshistproc | SANFORD HORNER BLVD. 230KV - CHATHAM STREET 23KV | 10/11/2018 14:44 | 10/11/2018 22:57 | 4883578 | OCB - ABC FID: T2440B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 1348 | 1953 | 493 | Node~T2440B03_1 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREES TREE HAS TORN DOWN PRIMARY AT G763AC HILL AVE AND LAWERENCE ST | ... NO OUTAGE REVIEW INFO
255 | Veg - MED35 | Asheboro | ASHEBORO SOUTH 115KV - ASHEBORO SOUTH 23KV | 10/11/2018 15:23 | 10/11/2018 18:00 | 4881552-1 | OCB - ABC FID: T0950B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 661 | 1830 | 157 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None RECLOSER STILL OFF AT 12EB24 | ... NO OUTAGE REVIEW INFO
256 | Veg - MED35 | Asheboro | ASHEBORO SOUTH 115KV - ASHEBORO SOUTH 23KV | 10/11/2018 15:23 | 10/12/2018 12:21 | 4881552-2 | RECLOSER - ABC FID: 12EB24_2302485 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 692 | 1830 | 1258 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None RECLOSER STILL OFF AT 12EB24 | ... NO OUTAGE REVIEW INFO
257 | Veg - MED35 | Asheboro | RAMSEUR 115KV - FRANKLINVILLE 24KV | 10/11/2018 15:24 | 10/11/2018 19:30 | 4881406 | RECLOSER - BC FID: 98G01_104574543 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 533 | 1996 | 246 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None restored tree fell on wire | ... NO OUTAGE REVIEW INFO
258 | Veg - MED35 | Asheboro | RAMSEUR 115KV - FRANKLINVILLE 24KV | 10/11/2018 15:26 | 10/11/2018 18:50 | 4881414-1 | OCB - ABC FID: T1390B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 906 | 1996 | 204 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE DOWN AT DIS# RECLOSER OPEN L129AD | ... NO OUTAGE REVIEW INFO
259 | Veg - MED35 | Asheboro | RAMSEUR 115KV - FRANKLINVILLE 24KV | 10/11/2018 15:26 | 10/11/2018 20:14 | 4881414-3 | RECLOSER - ABC FID: 98G01_104574543 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 1070 | 1996 | 288 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE DOWN AT DIS# RECLOSER OPEN L129AD | ... NO OUTAGE REVIEW INFO
260 | Veg - MED35 | Asheboro | ASHEBORO WEST 115KV - UWHARRIE STREET 23KV | 10/11/2018 15:28 | 10/11/2018 20:34 | 4882022 | RECLOSER - ABC FID: 128943_104203154 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 519 | 2792 | 306 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell on primary tree fell on primary | ... NO OUTAGE REVIEW INFO
261 | Veg - MED35 | Asheboro | ROBBINS 115KV - ROBBINS CITY 23KV | 10/11/2018 15:46 | 10/12/2018 19:40 | 4881740-2 | RECLOSER - ABC FID: 2089_2388107 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1055 | 1533 | 1674 |  | Tree/Vegetatn Limb Fell from Outside Right of Way None | ... NO OUTAGE REVIEW INFO
262 | Veg - MED35 | Roxboro | YANCEYVILLE 230KV - YANCEYVILLE PLEASANT GROVE 12KV | 10/11/2018 16:00 | 10/11/2018 17:05 | 4881969 | OCB - ABC FID: T5390B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1097 | 1098 | 64 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
263 | Veg - MED35 | Roxboro | YANCEYVILLE 230KV - MILTON 12KV | 10/11/2018 16:03 | 10/12/2018 12:00 | 4882060 | OCB - ABC FID: T5390B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1316 | 1315 | 1198 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None | ... NO OUTAGE REVIEW INFO
264 | Veg - MED35 | Chatham County | SILER CITY 115KV - ROCKY RIVER 24KV | 10/11/2018 16:14 | 10/11/2018 21:07 | 4882450-1 | SWITCH - ABC FID: 2335AF_2388946 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1434 | 1689 | 293 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None trees fell on feeder at 2219AF pulled top of pole out and broke insulators trees fell on feeder at 2219AF pulled top of pole out and broke insulators | ... NO OUTAGE REVIEW INFO
265 | Veg - MED35 | Chatham County | PITTSBORO 230KV - PITTSBORO 23KV | 10/11/2018 16:30 | 10/12/2018 12:42 | 4892785 | FUSE - ABC FID: AX25AF_2485227 | 03 Line Fuse | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 03 Wind | 552 | 2163 | 1212 |  | Tree/Vegetatn Tree/Limb Growth None | ... NO OUTAGE REVIEW INFO
266 | Veg - MED35 | Roxboro | ROXBORO 115KV - RIDGE ROAD 24KV | 10/11/2018 16:31 | 10/12/2018 18:32 | 4883300 | RECLOSER - A C FID: EXS02_2563621 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 608 | 1985 | 1561 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell on feeder 2 spans before regulator bank | ... NO OUTAGE REVIEW INFO
267 | Veg - MED35 | Henderson | HENDERSON NORTH 115KV - GREYSTONE 23KV | 10/11/2018 16:35 | 10/12/2018 13:10 | 4884803-1 | RECLOSER - ABC FID: 180B80_104569910 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 708 | 1438 | 1236 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None multiple fault locations | ... NO OUTAGE REVIEW INFO
268 | Veg - MED35 | Chatham County | PITTSBORO 230KV - PITTSBORO 23KV | 10/11/2018 16:37 | 10/13/2018 17:11 | 4894245 | LINE CUT - ABC FID: Line Cut-619479 | 09 Jumper/wire cut/open | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1163 | 2163 | 2914 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
269 | Veg - MED35 | Roxboro | ROXBORO SOUTH 230KV - BUSHY FORK 23KV | 10/11/2018 16:39 | 10/12/2018 09:00 | 4883190 | RECLOSER - C FID: 9T915_110989237 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 573 | 2516 | 982 |  | Tree/Vegetatn Limb Fell from Outside Right of Way None EXN06 tree on line EXN06 tree on line | ... NO OUTAGE REVIEW INFO
270 | Veg - MED35 | Chapel Hill AArias | JAMES ST - 19031207 | 10/11/2018 16:43 | 10/12/2018 15:03 | 10955650 | S-CKT - ABC Size: Class 1A FID: 38359365 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | 28 Other Species | 0 | F2 Forced Outage | 17 Wind and Rain | 2058 | 2059 | 1340 | aarias// 1603 N GREENSBORO ST | TREE AND LINES DOWN AT 1603 N GREENSBORO ST | aarias// MED - hurricane in area. 11 foot live cedar tree directly under the lines fell into the ckt. No equipment damage. Repairs delayed due to extensive damage. Ckt was last trimmed in 2018 ~~~ 10/25/2018 ¦ AArias ¦ Investigative Action
271 | Veg - MED35 | Chapel Hill AArias | JAMES ST - 19031206 | 10/11/2018 16:43 | 10/12/2018 11:11 | 10955448 | S-CKT - ABC Size: Class 1A FID: 38359281 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 14 Closed Breaker |  |  |  | F2 Forced Outage | 12 Hurricane | 1223 | 1749 | 1108 |  | related to event 10966200, circuit locked out due to weather and vegetation | aarias// hurricane in area. Extensive damage to ckt infrastructure due to vegetation, see tkt 10966200 ~~~ 10/22/2018 ¦ AArias ¦ Completion Codes or Remarks
272 | Veg - MED35 | Asheboro i25781 | ASHEBORO SOUTH 115KV - DIXIE DRIVE 23KV | 10/11/2018 16:45 | 10/11/2018 18:34 | 4884588-1 | OCB - ABC FID: T0950B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | OA Oak | 23 | F2 Forced Outage | 03 Wind | 1661 | 1764 | 109 | M506AD | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell on primary tree fell on primary | JWW// On 10/11/18 during hurricane Michael a large oak tree fell from outside of the right of way across all three phases burning two of the phases down locking out the Dixie Drive FCB causing 1717 customers to loose power. When the service tech arrived he opened up three solid blade disconnects at M509AD and had DCC energize the feeder this restored power to 1661 customers while leaving 56 customers out until the primary could be put back up. ~~~ 10/23/2017 ¦ i25781 ¦ Investigative Action
273 | Veg - MED35 | Chapel Hill AArias | CAMERON AVE - 19011201 | 10/11/2018 16:47 | 10/12/2018 06:57 | 10955607 | S-CKT - ABC Size: Class 2 FID: 50240605 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | TL Tree fails, NAC | DN No apparent defect | NA | MP Maple | 30 | F2 Forced Outage | 12 Hurricane | 1864 | 1864 | 850 | Merritt Mill Rd at the Hwy 54 on ramp | CMPL 2018-10-12 06:50:00 by SCHAMBE RMK: CIRCUIT LOCKOUT. TARGETS B-G. FMAG 3968. POSSIBLE FAULT LOCATION LOCUST CT & MERRITT MILL RD | aarias// MED - hurricane in area. Live maple tree fell from 30 ft away and was leaning on lines. No apparent defect and no equipment damage. Ckt was trimmed in 2016. Nothing found during field investigation ~~~ 10/24/2018 ¦ AArias ¦ Investigative Action
274 | Veg - MED35 | Chapel Hill AArias | EASTGATE RET - 19021205 | 10/11/2018 16:47 | 10/12/2018 19:42 | 10965471 | SOH - ABC Size: 600 Line Disconnect FID: 39040579 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | DN No apparent defect | 29 Conductor, bare | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 787 | 1010 | 1615 |  | Pike - CIRCUIT OUTAGE. TRIP 50. TARGETS A-B-C. FMAG 5048. TREE ON LINE NEAR S. LAKESHORE DR....REPAIRS MADE | aarias// MED - hurricane in area. Lines down reported at Old Oxford Rd due to a fallen tree, and at Markam Dr due to a fallen limb. Both are backbone locations. Backfeeding possible, but switching didn't happen. Repairs made and ckt restored ~~~ 10/18/2018 ¦ AArias ¦ Completion Codes or Remarks
275 | Veg - MED35 | Chapel Hill AArias | GREY - 19091208 | 10/11/2018 16:51 | 10/12/2018 10:21 | 10955930 | S-CKT - ABC Size: Class 3 FID: 38373035 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 1578 | 1579 | 1050 | aarias// intersection of 501 & Arlen Park Dr | CMPL 2018-10-12 10:33:00 by MWL0292 RMK: removed brk branch laying across xarm | aarias// hurricane in area. Removed broken live branch laying across xarm. Branch not found, and species/exact point of origin could not be determined during field investigation. No equipment damage ~~~ 10/22/2018 ¦ AArias ¦ Investigative Action
276 | Veg - MED35 | Chatham County omshistproc | PITTSBORO 230KV - BIG WOODS 23KV | 10/11/2018 16:51 | 10/12/2018 15:52 | 4882980 | OCB - ABC FID: T2250B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 1423 | 1427 | 1381 | Switch~T2250B02 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON WIRE | ... NO OUTAGE REVIEW INFO
277 | Veg - MED35 | Chatham County omshistproc | BYNUM 230KV - FEARRINGTON 24KV | 10/11/2018 16:52 | 10/12/2018 20:24 | 4888680 | SWITCH - ABC FID: 8BX83_2486879 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 852 | 1897 | 1651 | Node~1313011 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Hurricane Michael | ... NO OUTAGE REVIEW INFO
278 | Veg - MED35 | Chatham County | PITTSBORO 230KV - BIG WOODS 23KV | 10/11/2018 16:54 | 10/12/2018 16:34 | 4893765-2 | LINE CUT - ABC FID: Line Cut-618958 | 09 Jumper/wire cut/open | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 752 | 1427 | 1420 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None HURRICANE | ... NO OUTAGE REVIEW INFO
279 | Veg - MED35 | Durham rlw2159 | GREEN STREET - 14121209 | 10/11/2018 16:57 | 10/11/2018 21:14 | 10956245 | S-CKT - ABC Size: Class 1A FID: 38356269 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | EA Weather | TL Tree fails, NAC | DN No apparent defect | NA | BB Bamboo | 10 | F2 Forced Outage | 12 Hurricane | 2345 | 2425 | 257 | Swift Ave and Faber St | CMPL 2018-10-11 21:14:00 by SCHAMBE RMK: Bamboo tree had fallen into primary | rlw2159 med day hurricane Michael... Bamboo trees fell on primary at Swift Ave and Faber St ~~~ 10/19/2018 ¦ rlw2159 ¦ Investigative Action
280 | Veg - MED35 | Durham omshistproc | HOPE VALLEY - 14061205 | 10/11/2018 16:59 | 10/13/2018 13:26 | 10970422 | S-RCL - ABC Size: 560 WVE FID: 38998698 | 02 Line Recloser |  | 03 Vegetation | 03 Tree (Vegetation) | 16 Closed Recl or Sectionalizer |  |  |  | F2 Forced Outage |  | 535 | 695 | 2667 |  | 10/13/18 at 10:00 - Local Crews working WVE Recloser Subfeeder... Johnny 919-695-5617 | ... NO OUTAGE REVIEW INFO
281 | Veg - MED35 | Cary | GREEN LEVEL 115KV - WILSONVILLE 24KV | 10/11/2018 17:00 | 10/12/2018 12:19 | 4891520 | RECLOSER - ABC FID: CCY03_2585265 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 636 | 1403 | 1159 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None JEFF HUNLEY PIKE//919-270-1837 | ... NO OUTAGE REVIEW INFO
282 | Veg - MED35 | Durham AArias | GARRETT RD - 14202413 | 10/11/2018 17:04 | 10/12/2018 14:29 | 10967294 | S-RCL - ABC Size: 560 VWVE FID: 39008072 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | PT PINE | 35 | P4 Crew Initiated Outage | 12 Hurricane | 1186 | 5339 | 1285 | NC 54, between Hope Valley Rd & Park Ridge Rd | 6 SPANS 1 PH HW PRIMARY DOWN. BETWEEN POLE # 19HL64 & 19JJ00. FLAGGERS NEEEDED | aarias// MED - hurricane in area. Dead pine tree fell from 35 feet away in swampy area and tore field phase across 6 spans on double ckt line. No other equipment damage. Took out ckt (tkt 10956830). Sectionalized to restore ckt by opening SBs (tkt 10960779). Backfeeding options in place, but not executed. Ckt further sectionalized by opening Reclosers (tkts 10967294 & 10956829) and 80T (tkt 10967293) to minimize inrush. Ckt open again to close SBs (tkt 10967278). Nothing found on field investigation. Ckt scheduled to be proactively trimmed in 2019 ~~~ 11/26/2018 (45 days) ¦ AArias ¦ Investigative Action
283 | Veg - MED35 | Durham AArias | GARRETT RD - 14202413 | 10/11/2018 17:04 | 10/12/2018 13:02 | 10960779 | SOH - ABC Size: 600 Line Disconnect FID: 398736567 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | PT PINE | 35 | P4 Crew Initiated Outage | 12 Hurricane | 2051 | 5339 | 1198 | NC 54, between Hope Valley Rd & Park Ridge Rd | 6 SPANS 1 PH HW PRIMARY DOWN. BETWEEN POLE # 19HL64 & 19JJ00. FLAGGERS NEEEDED - OPENED CIRCUIT TO CLOSE IN SOLIDS- BACK ON UP TO RECLOSER 39009202 AND S-RCL: 39008072 | aarias// MED - hurricane in area. Dead pine tree fell from 35 feet away in swampy area and tore field phase across 6 spans on double ckt line. No other equipment damage. Took out ckt (tkt 10956830). Sectionalized to restore ckt by opening SBs (tkt 10960779). Backfeeding options in place, but not executed. Ckt further sectionalized by opening Reclosers (tkts 10967294 & 10956829) and 80T (tkt 10967293) to minimize inrush. Ckt open again to close SBs (tkt 10967278). Nothing found on field investigation. Ckt scheduled to be proactively trimmed in 2019 ~~~ 10/24/2018 ¦ AArias ¦ Investigative Action
284 | Veg - MED35 | Roxboro | BAHAMA 230KV - ROUGEMONT 23KV | 10/11/2018 17:05 | 10/12/2018 15:02 | 4884574 | OCB - ABC FID: T4555B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1906 | 1906 | 1317 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
285 | Veg - MED35 | Durham dlm4375 | CREST STREET - 14031210 | 10/11/2018 17:06 | 10/12/2018 12:36 | 10956382 | S-RCL - ABC Size: 800 VPST FID: 39007066 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | 03 Tree (Vegetation) | 16 Closed Recl or Sectionalizer |  | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 924 | 2161 | 1170 |  | RECLOSER OUTAGE. TARGETS A-B. FMAG UNAVAILABLE. POSSIBLE FAULT LOCATION AMERICAN DR & POTOMAC CT | dlm4375 med day hurricane Michael ... Lines down at American Dr & Constitution Dr due to trees ~~~ 10/22/2018 ¦ dlm4375 ¦ Completion Codes or Remarks
286 | Veg - MED35 | Cary | NEW HILL 230KV - NEW HILL 23KV | 10/11/2018 17:06 | 10/11/2018 21:35 | 4883305 | OCB - ABC FID: T5911B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 02 Rain | 1227 | 1226 | 269 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None breker is hot, crew to fix wire down at ABS94 and 8254K | ... NO OUTAGE REVIEW INFO
287 | Veg - MED35 | Durham dlm4375 | DURHAM MAIN - 14011219 | 10/11/2018 17:08 | 10/12/2018 21:15 | 10956490 | S-RCL - ABC Size: 560 WVE FID: 39007317 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 39 Repaired Overhead Conductor | 43 Recloser, Electronic |  |  | F2 Forced Outage | 12 Hurricane | 691 | 1256 | 1687 | 517 E club. | CMPL 2018-10-12 21:55:00 by VDB7113 RMK: 560 WVE RCL outage, 571 E Club Blvd-firemen marked w/ yellow tape line down in the water. Put up wire and removed limb. Recloser damaged bypassed FI39007317 | aarias// med day hurricane Michael.... line down in the water. Put up wire and removed limb. Recloser damaged bypassed ~~~ 10/22/2018 ¦ dlm4375 ¦ Completion Codes or Remarks
288 | Veg - MED35 | Cary omshistproc | NEW HILL 230KV - NEW HILL 23KV | 10/11/2018 17:08 | 10/12/2018 13:11 | 4889396 | SWITCH - ABC FID: 8022K_2553822 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 908 | 1226 | 1203 | Switch~8022K_2553822 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None tree down | ... NO OUTAGE REVIEW INFO
289 | Veg - MED35 | Durham dlm4375 | GREEN STREET - 14121202 | 10/11/2018 17:10 | 10/12/2018 09:29 | 10956522 | S-CKT - ABC Size: Class 1A FID: 38356185 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) | 14 Closed Breaker | 29 Conductor, bare | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 1217 | 1210 | 979 | unkown | CMPL 2018-10-12 09:33:00 by SJLINDE RMK: removed several small limbs from primary and also cleared a 6/3 svc from the neutral. city may have already cleared the tree or limb that took out the circuit. | dlm4375 med day hurricane Michael...removed several small limbs from primary and also cleared a 6/3 svc from the neutral. city may have already cleared the tree or limb that took out the circuit. ~~~ 10/22/2018 ¦ dlm4375 ¦ Completion Codes or Remarks
290 | Veg - MED35 | Henderson | OXFORD NORTH 230KV - OXFORD EAST 23KV | 10/11/2018 17:11 | 10/14/2018 17:15 | 4886021 | OCB - ABC FID: T5090B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 00 Calm | 1682 | 1019 | 4324 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree wire down broke pole at 307 salem rd | ... NO OUTAGE REVIEW INFO
291 | Veg - MED35 | Durham AArias | ENO - 14102402 | 10/11/2018 17:12 | 10/11/2018 19:41 | 10956574 | S-CKT - ABC Size: Class 1A FID: 38355849 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) |  |  |  |  | F2 Forced Outage | 17 Wind and Rain | 2011 | 2012 | 149 | Tree on line near I-85 | attempted to close breaker at 1850, did not hold...crew riding line back out....kwb | aarias// hurricane in area. Tree on line near I-85... NO OUTAGE REVIEW INFO
292 | Veg - MED35 | Durham AArias | POPE ROAD - 14082404 | 10/11/2018 17:13 | 10/12/2018 09:18 | 10963020 | S-RCL - ABC Size: 560 WVE FID: 39005117 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | PT PINE | 35 | P4 Crew Initiated Outage | 12 Hurricane | 1920 | 3258 | 965 | aarias// Winding Way & Chapel Hill Rd |  | aarias// MED - hurricane in area. Live pine tree snapped about 8 ft off the ground and fell from 35 ft away on a double ckt pole line and took out ckt (tkt 10956600). Two phases of primary down, no other equipment damage. Sectionalized to bring ckt back on by cutting jumpers in front of 3908 Old Chapel Hill Rd (tkt 10962265). Backfeeding options in place but not executed. Opened RCL 39005117 to minimize inrush while returning the ckt back to normal (tkt 10963020). Opened the ckt again to make up jumpers (tkt 10962965). Ckt was last trimmed in 2012 ~~~ 10/25/2018 ¦ AArias ¦ Investigative Action
293 | Veg - MED35 | Durham AArias | POPE ROAD - 14082404 | 10/11/2018 17:13 | 10/12/2018 01:49 | 10956600 | S-CKT - ABC Size: Class 2 FID: 38355933 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | TL Tree fails, NAC | DN No apparent defect | 29 Conductor, bare | PT PINE | 35 | F2 Forced Outage | 12 Hurricane | 884 | 3258 | 516 | aarias// Winding Way & Chapel Hill Rd | J388 CHRIS BRIGGS CUT JUMPERS TO SECTIONALIZE | aarias// MED - hurricane in area. Live pine tree snapped about 8 ft off the ground and fell from 35 ft away on a double ckt pole line and took out ckt (tkt 10956600). Two phases of primary down, no other equipment damage. Sectionalized to bring ckt back on by cutting jumpers in front of 3908 Old Chapel Hill Rd (tkt 10962265). Backfeeding options in place but not executed. Opened RCL 39005117 to minimize inrush while returning the ckt back to normal (tkt 10963020). Opened the ckt again to make up jumpers (tkt 10962965). Ckt was last trimmed in 2012 ~~~ 10/25/2018 ¦ AArias ¦ Investigative Action
294 | Veg - MED35 | Garner c72037 | DUNCAN 230KV - DUNCAN 24KV | 10/11/2018 17:15 | 10/11/2018 19:43 | 4883446 | RECLOSER - ABC FID: J805BH_103783585 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | TF Tree fails, defective | DA Damaged | 29 Conductor, bare | PT PINE | 36 | F2 Forced Outage | 12 Hurricane | 1224 | 2587 | 148 | K394BH | Missing Missing Missing | MHS- a 12" in DIA. defective pine tree with Knot broke about 20' from ground level and 36' from C/L taking down bottom phase and neutral. crew removed tree and did repairs. they then had DCC Re-energize the recloser at J805BH ~~~ 10/30/2018 (19 days) ¦ c72037 ¦ Investigative Action
295 | Veg - MED35 | Durham rlw2159 | ASHE STREET - 14021203 | 10/11/2018 17:15 | 10/11/2018 23:56 | 10956709 | S-CKT - ABC Size: Class 3 FID: 38355717 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | EA Weather | TL Tree fails, NAC | DN No apparent defect | 74 Wire, copper | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 603 | 2214 | 401 | 1007 North Guthrie Ave. | CMPL 2018-10-12 00:05:00 by SCHAMBE RMK: 1 phase primary down in front of 1007 N Guthrie Ave. Opened 3 80Ts at Holloway and N Guthrie to clear. | aarias// med day hurricane Michael....circuit out see 10956709 1 phase primary down in front of 1007 N Guthrie Ave tree on power line. Opened 3 80Ts (37 cust) see 10961916 at Holloway and N Guthrie to clear. Closed solid blades see 10943513 (932 cust) at feeder tied to backfeed from Oxford 1211 see 109425351 (677 customers) ~~~ 10/19/2018 ¦ rlw2159 ¦ Investigative Action
296 | Veg - MED35 | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 10/11/2018 17:18 | 10/12/2018 08:23 | 4883463 | RECLOSER - ABC FID: BR21BJ_104162335 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | PT PINE |  | F2 Forced Outage | 12 Hurricane | 1373 | 2736 | 905 | T492BJ | Tree/Vegetatn Limb Fell from Inside Right of Way None tree limb at T492BJ | MHS- a 2" in DIA. live pine tree limb broke out of tree and fell across all 3 phases locking out the recloser at BR21BJ. Crew cleared the limb off of the line and had DCC reenergize the Recloser ~~~ 10/18/2018 ¦ c72037 ¦ Investigative Action
297 | Veg - MED35 | Garner | HOLLY SPRINGS 230KV - BRACKENRIDGE 24KV | 10/11/2018 17:18 | 10/11/2018 22:22 | 4883496 | RECLOSER - AB FID: 17KQ26_104223094 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 03 Wind | 632 | 1824 | 304 |  | Tree/Vegetatn Tree/Limb Growth None cut tree growth out of primary feeder | ... NO OUTAGE REVIEW INFO
298 | Veg - MED35 | Durham AArias | GARRETT RD - 14202413 | 10/11/2018 17:21 | 10/12/2018 14:59 | 10956829 | S-RCL - ABC Size: 560 WVE FID: 39009202 | 02 Line Recloser | OH Distribution Line Overhead | EA Weather | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | PT PINE | 35 | P4 Crew Initiated Outage | 12 Hurricane | 1566 | 5339 | 1298 | NC 54, between Hope Valley Rd & Park Ridge Rd | RCL outage restored, lockout due to storm | aarias// MED - hurricane in area. Dead pine tree fell from 35 feet away in swampy area and tore field phase across 6 spans on double ckt line. No other equipment damage. Took out ckt (tkt 10956830). Sectionalized to restore ckt by opening SBs (tkt 10960779). Backfeeding options in place, but not executed. Ckt further sectionalized by opening Reclosers (tkts 10967294 & 10956829) and 80T (tkt 10967293) to minimize inrush. Ckt open again to close SBs (tkt 10967278). Nothing found on field investigation. Ckt scheduled to be proactively trimmed in 2019 ~~~ 10/24/2018 ¦ AArias ¦ Investigative Action
299 | Veg - MED35 | Durham omshistproc | HOPE VALLEY - 14061209 | 10/11/2018 17:21 | 10/12/2018 06:38 | 10956831 | S-RCL - ABC Size: 560 WVE FID: 39005849 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails |  |  |  |  | F2 Forced Outage | 12 Hurricane | 1182 | 2027 | 797 | removed loimb 3 spans from reclosure | M Farrish......Limb across OH pri/neu, at 3011 Academy Drive, Pilgram United Church of Christ, 6/3 street light cable down. | ... NO OUTAGE REVIEW INFO
300 | Veg - MED35 | Chapel Hill AArias | EASTGATE RET - 19021209 | 10/11/2018 17:25 | 10/12/2018 17:54 | 10956953 | S-CKT - ABC Size: Class 2 FID: 38359233 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | UN Unknown Species |  | F2 Forced Outage | 12 Hurricane | 1259 | 1262 | 1469 | aarias// Cleland Rd & Hamilton Rd | Pike - CIRCUIT OUTAGE. TARGETS A-B-C. FMAG 3337. POSSIBLE FAULT LOCATION CLELAND RD & HAMILTON RD, TREE ON LINE | aarias// hurricane in area. Tree on line @ Cleland Rd & Hamilton Rd ~~~ 10/18/2018 ¦ AArias ¦ Completion Codes or Remarks
301 | Veg - MED35 | Raleigh DFontan | CHESTNUT HILLS 115KV - HICKORY HILLS 23KV | 10/11/2018 17:31 | 10/11/2018 20:41 | 4883680 | RECLOSER - ABC FID: 17L247_104306148 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | TL Tree fails, NAC | DN No apparent defect | P2 Pole, CCA | OA Oak | 83 | F2 Forced Outage | 16 R Unknown | 1105 | 1600 | 190 | B510BK | Missing Missing Missing 2 BROKEN 45 C4 POLES, 4 SPANS OF 477 DOWN, 3 UG DIPS ON BROKEN POLES, NEED TREE CREW | Peel/Fontana 10/17/18: A 4' dia. x ~100' tall pin oak,83' from the line CL, was blown over from hurricane winds and fell into the feeder at pole B510BK, broke 2 poles and tore down 4 spans of the feeder backbone, locking out recloser 17L247. Responding crews sectionalized the feeder to isolate the damaged line section, and restored service from alternate sources, afterwhich the line section was rebuilt, and service was then fully restored. ~~~ 10/17/2018 ¦ DFontan ¦ Investigative Action
302 | Veg - MED35 | Raleigh e68825 | RALEIGH NORTHSIDE 115KV - GAVIN STREET 12KV | 10/11/2018 17:35 | 10/11/2018 21:30 | 4883727 | OCB - ABC FID: T5131B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | LL Tree limb fails | DV Visible stem decay | NA | SY Sycamore | 18 | F2 Forced Outage | 12 Hurricane | 1239 | 1245 | 235 | E070BK-E073BK | Natural Interf OH - Other (Comments) None tree limb in feeder at glascock & watuaga | PEEL/Fontana 10/18/18: A 1' dia. x 30' long diseased limb broke off 18' from the line CL from a 2.5' dia. x ~60' tall sycamore 18' off the line CL, and fell across the feeder in span E070BK-E073BK, locking out the FCB. Responding C&M Crew had a tree crew remove the limb from the line, then had DCC remotely close the FCB to restore service. No damage. ~~~ 10/18/2018 ¦ e68825 ¦ Investigative Action
303 | Veg - MED35 | Garner | GARNER WHITE OAK 230KV - CORNWALLIS 24KV | 10/11/2018 17:38 | 10/11/2018 20:30 | 4883758 | RECLOSER - A C FID: 5NG99_104520915 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 02 Rain | 910 | 1923 | 172 | Recloser~5NG99_104520915 | Tree/Vegetatn Limb Fell from Inside Right of Way None Tree limb removed. | ... NO OUTAGE REVIEW INFO
304 | Veg - MED35 | Cary | CARY 230KV - WEST CHATHAM STREET 23KV | 10/11/2018 17:40 | 10/12/2018 11:29 | 4883800-1 | RECLOSER - A FID: 17LT98_104265247 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 02 Rain | 766 | 3392 | 1069 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None removed and restored | ... NO OUTAGE REVIEW INFO
305 | Veg - MED35 | Henderson | OXFORD SOUTH 230KV - STEM 23KV | 10/11/2018 17:42 | 10/12/2018 20:11 | 4893210 | SWITCH - ABC FID: ES828_2891648 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 591 | 2535 | 1589 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None | ... NO OUTAGE REVIEW INFO
306 | Veg - MED35 | Raleigh | CHESTNUT HILLS 115KV - NORTH GLEN 23KV | 10/11/2018 17:47 | 10/12/2018 15:53 | 4883945 | RECLOSER - A C FID: E069BL_104130025 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1171 | 2553 | 1326 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
307 | Veg - MED35 | Raleigh | CHESTNUT HILLS 115KV - NORTH GLEN 23KV | 10/11/2018 17:48 | 10/12/2018 15:53 | 4883998 | RECLOSER - B FID: E069BL_104130025 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 722 | 2553 | 1324 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
308 | Veg - MED35 | Garner | GARNER TRYON HILLS 115KV - LOOP ROAD 24KV | 10/11/2018 17:51 | 10/11/2018 21:37 | 4884045 | RECLOSER - AB FID: DP32BJ_105710299 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 640 | 1865 | 226 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None tree limb btw GJ32BJ and GJ33BJ | ... NO OUTAGE REVIEW INFO
309 | Veg - MED35 | Raleigh DFontan | CHESTNUT HILLS 115KV - NORTH GLEN 23KV | 10/11/2018 17:54 | 10/11/2018 23:56 | 4884076 | WORK REQST - ABC FID: T4620B11 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | LR Tree limb, dead, overhang | D2 Dead | NA | OW Oak, willow |  | F2 Forced Outage | 12 Hurricane | 605 | 2553 | 362 | BZ96BL-8JA71 | Cust Prob Rqst Customer Request None lights on lights on | Peel/Fontana 10/17/18: A 2" dia. x 6' long dead limb broke out of the overhang of a 3' dia. x ~80' tall Willow Oak 8' off the line CL, and fell onto and lodged in the primary conductors in span BZ96BL-8JA71, causing an A-C fault, land locked out the FCB at 5:51:36 PM. Responding C&M crew removed the limb from the line & had DCC remotely close in the FCB to restore service to the feeder at 11:56 PM. We could not determine from where on the tree the limb broke off. No damage. ~~~ 10/17/2018 ¦ DFontan ¦ Investigative Action
310 | Veg - MED35 | Raleigh e68825 | MORDECAI 115KV - BLOUNT STREET 12KV | 10/11/2018 17:55 | 10/11/2018 22:16 | 4884079 | OCB - ABC FID: T5005B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | P1 Pole, Creosote | OA Oak | 40 | F2 Forced Outage | 12 Hurricane | 1107 | 1096 | 261 | RE014-G842BK | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell at g847bk, broken poles, partial restore in process. | Peel/Fontana 10/18/18: a 4' X ~60' tall oak, 40' off of line CL, uprooted and was blown over during hurricane winds and fell onto the feeder in span RE014-G842BK, breaking 2 poles and tearing down 4 spans of the feeder backbone, and locked out the FCB at 5:55 PM. Feeder was sectionalized to isolate the damaged section, and service was restored through alternate sources at 10:16PM. Damaged section was rebuilt and later rrenergized. ~~~ 10/18/2018 ¦ e68825 ¦ Investigative Action
311 | Veg - MED35 | Raleigh e68825 | LAKESTONE 115KV - LASSITER MILL 12KV | 10/11/2018 17:57 | 10/11/2018 22:28 | 4884098 | OCB - ABC FID: T4870B06 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LL Tree limb fails | DN No apparent defect | NA | OW Oak, willow | 14 | F2 Forced Outage | 12 Hurricane | 530 | 583 | 271 | E948BL | Missing Missing Missing | Peel/Fontana 10/19/18: A 1" dia. x 4' long broke off of a 2.5' dia. x ~60' tall willow oak 14' off of line CL, fell into the feeder at pole E948BL, causing an A-C phase-to-phase fault, and locked out the FCB. No damage. Limb was not found during original feeder patrols the night of the storm; the responding crew had DCC remotely close the FCB to restore service to the feeder (and it held). Upon finding the culprit in this fault area patrol, engineer called C&M to have limb removed from the line to preclude recurrence. No damage. ~~~ 10/19/2018 ¦ e68825 ¦ Investigative Action
312 | Veg - MED35 | Raleigh e68825 | LAKESTONE 115KV - COLEY FOREST 12KV | 10/11/2018 18:00 | 10/11/2018 23:52 | 4884121-3 | SWITCH - ABC FID: FT70BL_2867498 | 08 Disconnect | OH Distribution Line Overhead | 11 Unknown Cause | TF Tree fails, defective | DD Co-dominate stem | P1 Pole, Creosote | PP Yellow Poplar (tulip) | 50 | F2 Forced Outage | 12 Hurricane | 679 | 1176 | 352 | RBU90-RBU88 | Missing Missing Missing | PEEL 10/18/18: A 6' dia. x ~125' tall yellow poplar (Tulip), ~ 50' off the line CL, with co-dominant stem, on the edge of a creek bank, was blown down by hurricane force winds, and one stem fell into the feeder in span RBU90-RBU88, broke pole RBU90, and tore down 2 spans of feeder. Responding crew sectionalized the feeder to isolate the damaged line section and restore service to the feeder from alternate sources. Damaged line section was rebuilt and service restored later to this line section. ~~~ 10/18/2018 ¦ e68825 ¦ Investigative Action
313 | Veg - MED35 | Raleigh DFontan | METHOD 230KV - DIXIE TRAIL 12KV | 10/11/2018 18:00 | 10/11/2018 21:55 | 4884117 | OCB - ABC FID: T4990B39 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LD Tree limb, dead | D2 Dead | NA | MS Maple, sugar |  | F2 Forced Outage | 12 Hurricane | 1368 | 1367 | 235 | RB001-RB042 | Missing Missing Missing | Peel/Fontana 10/18/18: A 3" dia. x 10' long dead limb broke off a 2' diam. x 50' tall sugar maple 20' off of line CL, fell onto the feeder in span RB001-RB042, caused an A-B phase-to-phase fault, and locked out the FCB. No Damage. Could not determine from where on the tree the limb had broke off. Responding crew removed the limb and had DCC remotely close the FCB to restore service to the feeder. ~~~ 10/18/2018 ¦ DFontan ¦ Investigative Action
314 | Veg - MED35 | Roxboro | ROXBORO 115KV - RIDGE ROAD 24KV | 10/11/2018 18:03 | 10/12/2018 18:32 | 4892244 | RECLOSER - AB FID: EXS02_2563621 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 548 | 1985 | 1468 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TIED TO OUTAGE 4883300 | ... NO OUTAGE REVIEW INFO
315 | Veg - MED35 | Raleigh | RALEIGH EAST STREET 230KV - EAST STREET 12KV | 10/11/2018 18:03 | 10/13/2018 07:24 | 4884205 | SWITCH - ABC FID: DY51BK_2867598 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 603 | 852 | 2241 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None power came back on last night. | ... NO OUTAGE REVIEW INFO
316 | Veg - MED35 | Cary | CARY EVANS ROAD 230KV - WESTON 24KV | 10/11/2018 18:04 | 10/12/2018 15:58 | 4884296 | OCB - ABC FID: T4602B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 2716 | 2723 | 1314 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
317 | Veg - MED35 | Cary | GREEN LEVEL 115KV - GREEN LEVEL 24KV | 10/11/2018 18:05 | 10/12/2018 10:25 | 4884377-2 | SWITCH - ABC FID: 5523K_104248313 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 941 | 3251 | 980 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None FORM SENT | ... NO OUTAGE REVIEW INFO
318 | Veg - MED35 | Raleigh DFontan | RALEIGH HOMESTEAD 230KV - US 1 N 23KV | 10/11/2018 18:07 | 10/11/2018 21:51 | 4884438 | OCB - ABC FID: T5125B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LL Tree limb fails | DN No apparent defect | NA | PV Pine, Virginia |  | F2 Forced Outage | 12 Hurricane | 2590 | 2583 | 224 | 465BK-464BK | Missing Missing Missing | Peel/Fontana 10/17/18: A 1.5'" dia. x 7' long live limb broke off a 3' dia. x 60' tall Virginia Pine 20' off of line CL, and fell onto the feeder in span 465BK-464BK, causing an A phase to B phase fault, locking out the FCB. No Damage. We could not determine from where on the tree the limb broke off. Responding crew removed the limb, then had DCC remotely close the FCB to restore service to the feeder. ~~~ 10/17/2018 ¦ DFontan ¦ Investigative Action
319 | Veg - MED35 | Raleigh DFontan | CHESTNUT HILLS 115KV - CHESTNUT HILLS SWEETBRIAR 23KV | 10/11/2018 18:12 | 10/11/2018 20:51 | 4884571 | OCB - ABC FID: T4620B10 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | LL Tree limb fails | DN No apparent defect | NA | MV Maple, silver |  | F2 Forced Outage | 12 Hurricane | 1685 | 1656 | 159 | DJ01BK-DH99BK | Missing Missing Missing | Peel/Fontana 10/17/18: A 1" dia. x 8' long live limb broke off a 2' dia. x ~70' tall silver maple 38' off of the line CL and fell onto the feeder in span DJ01BK-DH99BK, causing a B phase to C phase fault, locking out the FCB. Responding crew removed the limb, and had DCC remotely close the FCB to restore service to the feeder. No damage. Could not determine from where on the tree the limb broke off. ~~~ 10/17/2018 ¦ DFontan ¦ Investigative Action
320 | Veg - MED35 | Garner c72037 | CLAYTON 115KV - GLENHAVEN 24KV | 10/11/2018 18:13 | 10/11/2018 21:49 | 4884628-3 | SWITCH - ABC FID: 1APQ82_107808321 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin | NA | PT PINE | 18 | F2 Forced Outage | 12 Hurricane | 720 | 1465 | 216 | FT88BJ | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree leaning into double circuit and glennhaven feeder, going to switch out glennhaven and barber mill feeder for tree crew to cut tree | MHS-A Live pine tree limb covered with vines weighted down by rain and wind came down across a double circuit locking out the Glenhaven FCB crew switched out the other feeder which is the Barbour Mill for Safety. After crew cleared both feeders they had DCC re-energizer the Glenhaven FCB and also re-energize the recloser on the Barbour Mill ~~~ 10/18/2018 ¦ c72037 ¦ Investigative Action
321 | Veg - MED35 | Garner c72037 | CLAYTON 115KV - GLENHAVEN 24KV | 10/11/2018 18:13 | 10/11/2018 21:25 | 4884628-2 | JUMPER - ABC FID: JUMPER-618158 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin | NA | PT PINE | 18 | F2 Forced Outage | 12 Hurricane | 552 | 1465 | 192 | FT88BJ | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree leaning into double circuit and glennhaven feeder, going to switch out glennhaven and barber mill feeder for tree crew to cut tree | MHS-A Live pine tree limb covered with vines weighted down by rain and wind came down across a double circuit locking out the Glenhaven FCB crew switched out the other feeder which is the Barbour Mill for Safety. After crew cleared both feeders they had DCC re-energizer the Glenhaven FCB and also re-energize the recloser on the Barbour Mill ~~~ 10/18/2018 ¦ c72037 ¦ Investigative Action
322 | Veg - MED35 | Raleigh e68825 | RALEIGH BLUE RIDGE 230KV - GLENWOOD AVENUE 23KV | 10/11/2018 18:18 | 10/11/2018 22:58 | 4884686 | OCB - ABC FID: T5122B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | DN No apparent defect | NA | OB Oak, white | 35 | F2 Forced Outage | 12 Hurricane | 1844 | 1857 | 280 | Load~FP41BL | Tree/Vegetatn Limb Fell from Inside Right of Way None 1 fault at FP41BL - recloser is bypassed | Peel/Fontana 10/19/18: A 2.5' dia. x ~60' tall white oak 35' off of the line CL uprooted and was blown over into the feeder at FP41BL during hurricane winds, causing an A phase to C phase fault, locking out the FCB. Responding crew sectionalized the feeder to isolate the faulted line section to have a tree crew remove the tree, then had DCC remotely close the FCB to restore service to the feeder. No damage! Recloser FP41BL was not in commission and the responding C&M crew opened up the disconnects at the recloser and have DCC reclose the breaker to restore the remainder of the feeder. While the disconnects were open crews were able to make the necessary repairs. ~~~ 10/19/2018 ¦ e68825 ¦ Investigative Action
323 | Veg - MED35 | Garner | CLAYTON 115KV - TV 24KV | 10/11/2018 18:21 | 10/12/2018 10:20 | 4884882 | RECLOSER - ABC FID: ND17BJ_1624697 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 11 Tornado/Wind Shear/Microburst | 528 | 1916 | 959 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None cut tree and cleared from line cutting tree to clear from line | ... NO OUTAGE REVIEW INFO
324 | Veg - MED35 | Raleigh | CHESTNUT HILLS 115KV - CHESTNUT HILLS SWEETBRIAR 23KV | 10/11/2018 18:21 | 10/11/2018 21:50 | 4888843 | SWITCH - ABC FID: DH36BK_2867621 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1310 | 1656 | 209 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None Hurricane Michael Hurricane Michael | ... NO OUTAGE REVIEW INFO
325 | Veg - MED35 | Raleigh e68825 | RALEIGH TIMBERLAKE 115KV - BRENTWOOD 23KV | 10/11/2018 18:22 | 10/11/2018 22:19 | 4888252 | SWITCH - ABC FID: 14AH05_1228102 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | TF Tree fails, defective | DC Internal stem decay | NA | PV Pine, Virginia | 68 | F2 Forced Outage | 12 Hurricane | 2199 | 2195 | 237 | AZ85BK-AZ86BK | Missing Missing Missing | Peel/Fontana 10/18/18: A 1.5' dia. x ~90' tall Virginia Pine, 68' off of the line CL, broke at 4' above the GL and fell into the Brentwood 23kV and Highwoods 23kV feeders double circuit span AZ85BK-AZ86BK due to hurricane winds and internal stem decay, and locked out both feeders. Responding crew sectionalized both feeders, isolated both feeders faulted line section to enable tree crew to remove the tree, and restored service to both feeders through alternate sources. After tree crews removed the tree from the line, the responding crew had DCC close both FCBs to restore service to the remainder of both feeders. No damage! ~~~ 10/18/2018 ¦ e68825 ¦ Investigative Action
326 | Veg - MED35 | Henderson | OXFORD SOUTH 230KV - STEM 23KV | 10/11/2018 18:23 | 10/12/2018 13:07 | 4893052 | RECLOSER - ABC FID: ES701_2892182 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 00 Calm | 661 | 2535 | 1125 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
327 | Veg - MED35 | Zebulon i70604 | ZEBULON 115KV - ZEBULON WEST 23KV | 10/11/2018 18:26 | 10/11/2018 19:15 | 4885067 | OCB - ABC FID: T6090B11 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | PT PINE |  | F2 Forced Outage | 12 Hurricane | 1927 | 1946 | 49 | C860BF | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None hurricane hurricane | CPS// Pine limb fell from outside of R/W near C860BF causing circuit breaker to open // No damage to equipment // Limb was removed and all customers restored // ~~~ 10/18/2018 ¦ i70604 ¦ Investigative Action
328 | Veg - MED35 | Selma | FOUR OAKS 230KV - HANNAHS CREEK 24KV | 10/11/2018 18:26 | 10/12/2018 06:23 | 4885032 | RECLOSER - ABC FID: V901_104479318 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 925 | 1553 | 717 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None associated with reclosure V901 | ... NO OUTAGE REVIEW INFO
329 | Veg - MED35 | Henderson | FRANKLINTON 115KV - MITCHINERS CROSSROADS 24KV | 10/11/2018 18:41 | 10/13/2018 21:26 | 4885440-1 | RECLOSER - A FID: EGT75_104569898 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 520 | 1401 | 3045 |  | Tree/Vegetatn Limb Fell from Outside Right of Way None pine tree fell on line pine tree fell on line | ... NO OUTAGE REVIEW INFO
330 | Veg - MED35 | Zebulon omshistproc | NASHVILLE 115KV - RED OAK 23KV | 10/11/2018 19:08 | 10/12/2018 17:11 | 4887573 | OCB - ABC FID: T5900B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 1607 | 2049 | 1323 | Switch~T5900B02 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None Broke pole at dis# AX55BC Broke pole at dis# AX55BC | ... NO OUTAGE REVIEW INFO
331 | Veg - MED35 | Zebulon | SPRING HOPE 115KV - SPRING HOPE 23KV | 10/11/2018 19:34 | 10/12/2018 17:51 | 4888923 | RECLOSER - BC FID: 1B2E40_108856090 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 526 | 1807 | 1337 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None tree fell on primary and opened | ... NO OUTAGE REVIEW INFO
332 | Veg - MED35 | Zebulon i70604 | CASTALIA 230KV - HOLLISTER 24KV | 10/11/2018 20:04 | 10/11/2018 21:48 | 4887877 | OCB - ABC FID: T6040B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | NA | PP Yellow Poplar (tulip) | 22 | F2 Forced Outage | 12 Hurricane | 1583 | 1675 | 104 | B931 | Tree/Vegetatn Limb Fell from Outside Right of Way None limb on feeder near freeman rd. | CPS// Poplar limb broke and fell on conductor near dis#B931 // Limb broke 22' from center line // No damage to equipment // Limb was removed and all customers restored ~~~ 10/17/2018 ¦ i70604 ¦ Investigative Action
333 | Veg - MED35 | Cary | GREEN LEVEL 115KV - WIMBERLY ROAD 24KV | 10/11/2018 20:39 | 10/12/2018 02:49 | 4888735 | RECLOSER - A C FID: B017K_104362626 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 00 Calm | 934 | 1736 | 370 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
334 | Veg - MED35 | Chatham County | SILER CITY HIGHWAY 64 230KV - SILER CITY HIGHWAY 64 CENTRAL 24KV | 10/11/2018 21:08 | 10/11/2018 22:22 | 4889071 | RECLOSER - A C FID: 6HV05_104617066 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 03 Wind | 865 | 286 | 74 |  | Tree/Vegetatn Tree/Limb Growth None | ... NO OUTAGE REVIEW INFO
335 | Veg - MED35 | Raleigh | CHESTNUT HILLS 115KV - HICKORY HILLS 23KV | 10/11/2018 21:08 | 10/13/2018 20:58 | 4889504 | SWITCH - ABC FID: B875BK_2867661 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 04 Wind, Rain and Lightning | 959 | 1600 | 2869 | Node~1886443 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
336 | Veg - MED35 | Chatham County | SILER CITY HIGHWAY 64 230KV - SILER CITY HIGHWAY 64 CENTRAL 24KV | 10/11/2018 21:17 | 10/12/2018 14:38 | 4889510 | RECLOSER - ABC FID: 55K50_2379465 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 03 Wind | 783 | 286 | 1041 |  | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None reclosers locked out due to a tree tearing the primary and neutral down reclosers locked out due to a tree tearing the primary and neutral down | ... NO OUTAGE REVIEW INFO
337 | Veg - MED35 | Chatham County | SILER CITY HIGHWAY 64 230KV - SILER CITY HIGHWAY 64 CENTRAL 24KV | 10/11/2018 21:24 | 10/12/2018 15:09 | 4889564 | FUSE - ABC FID: 2957AF_111969306 | 03 Line Fuse | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 913 | 286 | 1065 |  | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
338 | Veg - MED | Durham C80721 | POPE ROAD - 14082409 | 10/13/2018 18:32 | 10/14/2018 14:27 | 10973937 | SOH - ABC Size: 600 Line Disconnect FID: 84666186 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 17 Closed Switch | P1 Pole, Creosote | NA R |  | F2 Forced Outage | 12 Hurricane | 664 | 1188 | 1195 |  | SCT OWENBY/CORN AT FID 38527216 BROKEN 45/3 POLE WITH 10 FT FB ARM AND 80T TAP FUSE/1 SPAN SINGLE PHASE 1/0 PRI & NEU DOWN/WIRES ACROSS RD/THREE PHASE IS STILL OUT SCT OWENBY/CORN SEE REMARKS FOR EVENT # 10972736 | aarias//BROKEN 45/3 POLE WITH 10 FT FB ARM AND 80T TAP FUSE/1 SPAN SINGLE PHASE 1/0 PRI & NEU DOWN/WIRES ACROSS RD/THREE PHASE IS STILL OUT SCT OWENBY/CORN SEE REMARKS FOR EVENT # 10972741 BROKEN 45/3 POLE WITH 10 FT FB ARM AND 80T TAP FUSE/1 SPAN SINGLE PHASE 1/0 PRI & NEU DOWN/WIRES ACROSS RD/THREE PHASE IS STILL OUT SCT OWENBY/CORN SEE REMARKS FOR EVENT # 10972736 ~~~ 10/26/2018 ¦ C80721 ¦ Completion Codes or Remarks
339 | Veg - MED | Durham omshistproc | POPE ROAD - 14082409 | 10/13/2018 18:32 | 10/13/2018 18:55 | 10973869 | S-CKT - ABC Size: Class 1A FID: 38356053 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | 03 Tree (Vegetation) |  |  |  |  | F2 Forced Outage | 12 Hurricane | 520 | 1188 | 23 |  |  | ... NO OUTAGE REVIEW INFO
340 | Veg | Cary | AMBERLY 230KV - GREEN HOPE 24KV | 10/15/2018 16:27 | 10/15/2018 17:49 | 4896794-2 | SWITCH - ABC FID: 11Y914_2670799 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 00 Calm | 501 | 3010 | 82 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None Tree on line. | ... NO OUTAGE REVIEW INFO
341 | Veg | Cary | AMBERLY 230KV - GREEN HOPE 24KV | 10/15/2018 16:27 | 10/15/2018 16:40 | 4896794-1 | SWITCH - B FID: 5ZC88_2681973 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | 37 Removed Limb or Tree From Lin |  |  | 5 | F2 Forced Outage | 00 Calm | 1171 | 3010 | 13 |  | Tree/Vegetatn Limb Fell from Inside Right of Way None Tree on line. | ... NO OUTAGE REVIEW INFO
342 | Veg | Raleigh DFontan | RALEIGH 115KV - SAINT MARYS STREET 12KV | 10/20/2018 08:29 | 10/20/2018 09:20 | 4898544 | OCB - ABC FID: T5160B09 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect | 37 Arrester | OW Oak, willow |  | F2 Forced Outage | 00 Calm | 851 | 1062 | 51 | Load~REB46 | Tree/Vegetatn Limb Fell from Inside Right of Way None limb fell across 3 cutouts @ reb46 | PEEL?Fontana - A 1/2" dia. x 4' long live limb fell from a 3.5' dia. x ~70' tall willow oak, 23' off of the line CL, lodged into the primary risers of the 2-pot xfmr bank on pole REB46, causing the FCB to lockout under an A-B-N fault at 8:29:34 AM. Pole, crossarm, and 1 of the cutout fuse barrel was charred, and a LA wildlife protector cap was blown off. Responding crewman removed the limb, then had DCC remotely close the FCB to restore service at 9:20:49 AM. We could not ascertain from exactly where on the tree the limb came. ~~~ 10/22/2018 ¦ DFontan ¦ Investigative Action
343 | Veg | Zebulon i70604 | SPRING HOPE 115KV - TAYLORS CROSSROADS 23KV | 10/21/2018 03:59 | 10/21/2018 05:00 | 4899185-1 | OCB - ABC FID: T6041B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | HT Tie, hand | SZ Sweet Gum | 45 | F2 Forced Outage | 03 Wind | 2110 | 2058 | 61 | Line~RF775_REL02_1175936 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE ON LINE BV69BC | CPS// Sweet gum tree located 45' from center line fell contacting conductor causing the circuit breaker to open // Tree was located in a swampy area surrounded by water // Damage to equipment included broken tie wire on middle phase ~~~ 10/23/2018 ¦ i70604 ¦ Investigative Action
344 | Veg | Henderson i67431 | HENDERSON NORTH 115KV - FARM STREET 23KV | 10/23/2018 14:11 | 10/23/2018 15:14 | 4900226-1 | OCB - ABC FID: T4770B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead |  | MP Maple | 25 | F2 Forced Outage | 00 Calm | 1251 | 1242 | 63 | Line~EJL36_EJL37_1644866 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | DPW: There were two faults involved in this outage event. The first was a hardwood limb that fell onto all 3 phases of the conductor, locking out the breaker. There was a contract crew installing new poles at the time. They cut the limb off the feeder and DCC was asked to close in the breaker. However, before it could be closed back in a dead tree (in the photo) fell onto the feeder. This tree was cut off the feeder and DCC energized the breaker. ~~~ 10/24/2018 ¦ i67431 ¦ Investigative Action
345 | Veg | Henderson omshistproc | HENDERSON NORTH 115KV - FARM STREET 23KV | 10/23/2018 15:23 | 10/23/2018 15:44 | 4900272-1 | RECLOSER - ABC FID: 18HB52_109512887 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | LX Trees, overgrown primary | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 00 Calm | 1150 | 1242 | 21 | Source~T4770 | Tree/Vegetatn Tree/Limb Growth None | ... NO OUTAGE REVIEW INFO
346 | Veg | Durham rlw2159 | CREST STREET - 14031210 | 10/26/2018 10:04 | 10/26/2018 10:49 | 10991215 | S-CKT - ABC Size: Class 1A FID: 38355381 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LL Tree limb fails | DN No apparent defect |  | MP Maple | 5 | F2 Forced Outage | 17 Wind and Rain | 2131 | 2161 | 45 | beside pole 1A7Y92 | CMPL 2018-10-26 10:52:00 by RAH6412 RMK: Circuit lockout, FMAG 3233 Targets AB jrknott, Halos on Morreene rd between Mordecai st and Campus Walk Ave | dlm4375 fireworks...911 called in at 1315 Morreene Rd branch on powerline ....circuit out FMAG 3233 Targets AB jrknott, Halos on Morreene rd between Mordecai st and Campus Walk Ave, big tree branch on line at corner of morreene rd and erwin rd close to apts. There was a live maple limb that fell out of live tree onto the circuit. This was about 5' from from the line. ~~~ 10/29/2018 ¦ rlw2159 ¦ Investigative Action
347 | Veg | Raleigh DFontan | LAKESTONE 115KV - BECKANA 12KV | 10/26/2018 16:13 | 10/26/2018 17:04 | 4901516 | OCB - ABC FID: T4870B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead | NA | MV Maple, silver |  | F2 Forced Outage | 00 Calm | 1035 | 1020 | 51 | Line~E459BL_E460BL_2846952 | Tree/Vegetatn Tree/Limb Growth None | Peel/Fontana 10/29/18: A 1" dia. x 8' long dead limb broke off of a 3' dia. x ~75' tall Silver Maple 23' off of the line CL, fell onto the feeder in span E459BL-E460BL, causing a C phase-to-ground fault, and the FCB to lock-out. Responding C&M tech removed the limb and had DCC remotely close the FCB to restore service to the feeder. We could not determine from where on the tree the limb broke off. No damage. ~~~ 10/29/2018 ¦ DFontan ¦ Investigative Action
348 | Veg | Raleigh DFontan | RALEIGH 115KV - SAINT MARYS STREET 12KV | 10/26/2018 16:38 | 10/26/2018 17:41 | 4901525 | OCB - ABC FID: T5160B09 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DR Roots rotten/defective | NA | OA Oak | 48 | F2 Forced Outage | 04 Wind, Rain and Lightning | 853 | 1062 | 63 | RBQ24-RBQ30 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE @ RBQ30 | Peel/Fontana 10/29/18: A 3' dia. x ~ 75' tall Bear Oak, 48' off of the line CL, uprooted and fell across the road and into the feeder in span RBQ30-RBQ24 (near RBQ30), and locked out the FCB. It appeared the tree was suffering from root rot. The tree was removed from the road and the line, then DCC remotely closed the FCB to restore service to the feeder. No damage. Customer count seems low because DOT was working under a section of the feeder and we de-energized a portion of the line so DOT could safely work. The remaining 220 customers were switched onto the Bishops Park 12kV feeder. ~~~ 10/29/2018 ¦ DFontan ¦ Investigative Action
349 | Veg | Henderson i67431 | WARRENTON 115KV - NORLINA 23KV | 10/26/2018 19:41 | 10/26/2018 20:56 | 4901635-1 | OCB - ABC FID: T5360B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | LD Tree limb, dead | D2 Dead |  | MP Maple | 22 | F2 Forced Outage | 00 Calm | 1700 | 1703 | 75 | EA705 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None TREE FELL AND CLAERED ITS SELF | DPW: The Norlina 23KV Feeder out of the Warrenton 115KV Substation locked out at 91:41pm affecting 1,704 customers. The outage was caused by a tree limb that fell on the line from outside the right of way. The Service Tech cleared the tree limb. The feeder was restored at 20:56pm for a duration of 74 minutes. Total CMI 127,701. ~~~ 10/29/2018 ¦ i67431 ¦ Investigative Action
350 | Veg | Zebulon i70604 | KNIGHTDALE 115KV - KNIGHTDALE INDUSTRIAL 24KV | 10/26/2018 21:35 | 10/26/2018 22:20 | 4901702-1 | OCB - ABC FID: T4850B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | SZ Sweet Gum | 27 | F2 Forced Outage | 00 Calm | 1993 | 2003 | 45 | GN49BF | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None TREE ON LINE | CPS// Dead Sweet Gum tree 27' from center line fell on conductor near dis#GN49BF causing the circuit breaker to open // Responding Service Tech removed tree from line and DCC re-energized the circuit breaker // No damage to equipment ~~~ 10/31/2018 ¦ i70604 ¦ Investigative Action
351 | Veg | Asheboro i25781 | RAMSEUR 115KV - COLERIDGE 24KV | 10/26/2018 21:52 | 10/26/2018 23:11 | 4901709 | RECLOSER - AB FID: 1740AD_104153226 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | NA | PT PINE | 18 | F2 Forced Outage | 02 Rain | 739 | 1469 | 79 | 2375AD | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None trees | JWW// On 10/26/18 at 09:52pm a dead pine tree fell at 2375AD locking out A and B phase causing 739 customers to loose power. When the service tech arrived he had DCC drop c phase which had 313 customers on it so he could cut the tree off of the 3 phase. After cutting the tree off of the Primary he had DCC energize the G&W restoring power to all 1052 customers. ~~~ 11/1/2018 ¦ i25781 ¦ Investigative Action
352 | Veg | Cary omshistproc | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 11/1/2018 18:28 | 11/1/2018 20:01 | 4903661-2 | OCB - ABC FID: T4866B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TL Tree fails, NAC | 37 Removed Limb or Tree From Lin |  |  | 30 | F2 Forced Outage | 03 Wind | 991 | 2825 | 93 | Line~B962BH_B963BH_2726355 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None | ... NO OUTAGE REVIEW INFO
353 | Veg | Raleigh e68825 | LEESVILLE WOOD VALLEY 230KV - BAILEYWICK ROAD 24KV | 11/2/2018 19:39 | 11/2/2018 21:37 | 4904027-1 | RECLOSER - BC FID: 79L17_112103687 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | TD Tree fails, dead | D2 Dead | 29 Conductor, bare | HW HARDWOOD | 16 | F2 Forced Outage | 04 Wind, Rain and Lightning | 857 | 1627 | 118 | FR17BL-FR15BL | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None Back lot lines down near Norwood Rd bridge. Back lot lines down near Norwood Rd bridge. | PEEL 11/7/18: A 1' dia. x ~90' tall dead HW, 16' off of the line CL, rotten at the base, broke at the GL and fell onto the fdr. in span FR17BL-FR15BL, broke B&C phase and neutral conductors , locking out B&C phases of recloser 79L17. Responding C&M tech switched to isolate the damaged line section for repairs and restored service to the feeder from alternate sources. ~~~ 11/5/2018 ¦ e68825 ¦ Investigative Action
354 | Veg | Durham rlw2159 | GREEN STREET - 14121210 | 11/2/2018 21:22 | 11/3/2018 01:01 | 10998716 | S-CKT - ABC Size: Class 3 FID: 38356353 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | TF Tree fails, defective | DE Erosion/poor enviornment | 29 Conductor, bare | OW Oak, willow | 1 | F2 Forced Outage | 17 Wind and Rain | 1878 | 1889 | 219 | 1111 OAKLAND AVE | CMPL 2018-11-03 01:28:00 by CCARTER RMK: LOCK OUT...TARGETS CG & FMAG 3550....@ 1109 OAKLAND AVENUE, SPAN OF PRIMARY DOWN DUE TO TREE LIMB DAMAGE PWR OUT TO NEIGHBORHOOD | rlw2159..Rainy and windy in area....circuit out due to Willow Oak tree falling at 1111 Oakland Ave. which damaged overhead primary. received 911 call of tree on fire and overhead primary on ground. see circuit blink 10998715 ~~~ 11/5/2018 ¦ rlw2159 ¦ Investigative Action
355 | Dist | Henderson i67431 | WARRENTON 115KV - NORLINA 23KV | 7/2/2018 22:03 | 7/2/2018 23:38 | 4735052-3 | SWITCH - ABC FID: EA588_1862127 | 08 Disconnect | OH Distribution Line Overhead | 04 Wildlife | 04 Wildlife | 29 Permanent Repair |  | J5 Snake | 0 | F2 Forced Outage | 00 Calm | 1395 | 1703 | 95 | Load~EA714 | Natural Interf OH - Animal/Bird (Comments) None snake on 3phase at EA714. burned down primary | DPW: The Norlina 23KV Feeder out of the Warrenton 115KV Substation locked out at 10:03PM on 7/2. A snake was found on the 3phase line at DIS#EA714, and the primary was burned down. Step restoration was performed to restore customers as follows: 204 customers were restored at 11:17PM and 1,397 customers were restored at 11:41PM. Repairs were complete and the remaining 92 customers were restored at 1:34AM on 7/3. ~~~ 7/5/2018 ¦ i67431 ¦ Investigative Action
356 | Dist | Durham AArias | RESEARCH TRIANGLE RET - 14052402 | 7/3/2018 14:36 | 7/3/2018 16:58 | 10814333 | S-RCL - ABC Size: 560 WVE FID: 39006985 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 16 Closed Recl or Sectionalizer | NA | UN Unknown Species |  | F2 Forced Outage | 00 Calm | 624 | 2562 | 142 | NO CAUSE FOUND | RCL outage...TL528/LUKE, TL526/LINDENMUTH, TL573/JACKSON. RODE OUT BACK BONE AND NO PROBLEM FOUND. BLOCKED RECLOSER AND CLOSED- NO PROBLEM FOUND. | aarias// rode ckt and found no apparent cause. Backlot power lines are clear of vegetation. Mark Leverett inspected unit and found decayed power cable to modem needing to be replaced. RCL was not left blocked by crew. Mark Leverett will pull data from control module to verify outage times and phases. ~~~ 7/5/2018 ¦ AArias ¦ Investigative Action
357 | Dist | Cary JOCHRIS | APEX 230KV - APEX HIGHWAY 55 23KV | 7/5/2018 09:07 | 7/5/2018 10:51 | 4736195 | RECLOSER - ABC FID: 9RK98_104607789 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 17 Tree error, public | 29 Permanent Repair | P6 R Pole, Fiberglass | MR Maple, red | 23 | F2 Forced Outage | 00 Calm | 1909 | 2086 | 104 | Line~10YE85_10YE84_2665974 | Human Interf Tree Cut on Line (By Logger or Customer) None Tree cut on line at 10YE84. Bryan M. Tree cut on line at 10YE84. Bryan M. | O. Christian - 10/3/2018 - 36" diameter maple tree 23' from CL cut down onto line by customer clearing a lot to build on breaking CCA pole 10YE84 and bringing down all three phase conductors and the neutral. New pole set conductors pulled and service restored. ~~~ 10/3/2018 (90 days) ¦ JOCHRIS ¦ Investigative Action
358 | Dist | Sanford i25781 | SANFORD GARDEN STREET - SOUTH HORNER 23KV | 7/5/2018 14:41 | 7/5/2018 15:21 | 4736347-2 | SWITCH - ABC FID: 3158AC_2494034 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 923 | 1585 | 40 | Load~S417AC | Human Interf OH - Vehicle None CRANE IN FEEDER | JWW...On 7/5/18 at 14:41 a truck that picks up grease from restaurants left boom up while driving and caught the telephone cable and broke the top out of the feeder pole at S417AC causing 1583 to loose power. When the crew arrived they opened up the air break switch at R437AC and had DCC close the FCB back in at 14:55 restoring power to 559 customers. The crew then opened the disconnects at 100F72 and closed air break switch at 3158AC at 15:21 tying the SOUTH HORNER BLVD with the WOODLAND AVE FDR restoring power to 923 customers leaving 101 customers out while replacing the broke pole. After replacing the broke pole the crew switched everything back to normal at 17:55 restoring power to the remaining 101 customers. ~~~ 7/6/2018 ¦ i25781 ¦ Investigative Action
359 | Dist | Sanford i25781 | SANFORD GARDEN STREET - SOUTH HORNER 23KV | 7/5/2018 14:41 | 7/5/2018 14:55 | 4736347-1 | OCB - ABC FID: T2432B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 559 | 1585 | 14 | Load~S417AC | Human Interf OH - Vehicle None CRANE IN FEEDER | JWW...On 7/5/18 at 14:41 a truck that picks up grease from restaurants left boom up while driving and caught the telephone cable and broke the top out of the feeder pole at S417AC causing 1583 to loose power. When the crew arrived they opened up the air break switch at R437AC and had DCC close the FCB back in at 14:55 restoring power to 559 customers. The crew then opened the disconnects at 100F72 and closed air break switch at 3158AC at 15:21 tying the SOUTH HORNER BLVD with the WOODLAND AVE FDR restoring power to 923 customers leaving 101 customers out while replacing the broke pole. After replacing the broke pole the crew switched everything back to normal at 17:55 restoring power to the remaining 101 customers. ~~~ 7/6/2018 ¦ i25781 ¦ Investigative Action
360 | Dist | Garner c72037 | FUQUAY 230KV - SUNSET PLAZA 23KV | 7/5/2018 16:04 | 7/5/2018 18:35 | 4736532-1 | SWITCH - ABC FID: G9B99_2636499 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | D4 Burned/Exploded | M3 Copper | 39 Disconnect | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 596 | 1617 | 151 | GNB35 | Overhead Fac Undetermined Feeder Circuit Breaker Lockout | MHS-the 600 AMP disconnects and T-Mods Burnt up at GNB35 causing fault on line, Locking out the Sunset Plaza FCB. Crew than did switching to back feed the line they first cleared the 600 AMP Disconnects and had DCC hot back up FCB getting 136 customers on. They then closed A/B switch G9B99 and got 596 customers back on did a few more switches to get the rest of the customers back on. did a W/O 29055805 to Replace Disconnects and T-MODS at GNB35 ~~~ 7/12/2018 ¦ c72037 ¦ Work Order(s) Generated
361 | Dist | Raleigh e68825 | PINE LAKE 230KV - WAKE FOREST 24KV | 7/6/2018 11:13 | 7/6/2018 11:21 | 4736882-1 | OCB - ABC FID: T5108B04 | 01 Feeder Breaker/Recl in Substa | UG Distribution Line Underground | 20 Equipment failure | 08 Error, Duke | 56 Sectionalized/Restored Servic | F2 Fuse Link | SD S&C Electric |  | P4 Crew Initiated Outage | 00 Calm | 1446 | 1062 | 8 | Fuse~MB733_1200576 | Undergrnd Fac Underground Switch Failure PM Switch Failed During Switching fuse smoking in comp #3 - mb733 | Fontana/Peel 7/9/18 - During switching (under DCC's guidance & permission), Crew discovered that a fuse in PMH MB733 compartment 3 became overloaded & was melting/smoking. Crew requested the DCC operator to open the Wake Forest 24kV FCB long enough for to clear the damaged fuse, then had DCC remotely closed the FCB back in to restore power. The feeder was out for about 8 minutes. ~~~ 7/9/2018 ¦ e68825 ¦ Investigative Action
362 | Dist | Zebulon i70604 | KNIGHTDALE 115KV - KNIGHTDALE WEST 24KV | 7/6/2018 16:06 | 7/6/2018 16:42 | 4737121 | RECLOSER - BC FID: F271BF_113931149 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | DE Prior damage | M2 ACSR | 29 Conductor, bare | UU Unknown Manufacturer |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 591 | 1971 | 36 | Line~GP08BF_GP09BF_1622229 | Overhead Fac Overhead Connections / Jumper Failure Jumper Burned In Two see main outage 4737096 - open other two phase to clear down line | CPS//ACSR conductor burned down mid span at dis#GP08BF causing A phase to open at G&W F271BF.(Reflected in Out#4737096) Responding service tech opened B & C phase in order to make repairs. (Reflected in Out#4737121) Found pine stump that had been pulled up on one side next to where line burned down. It appears the wire failure was caused by prior damage from tree. Note: RUSD WR 25025322 would have saved 359 customers from an interruption with the installation of Reclosers at F395BF. WR Targeted Finish date was 1/5/2018 ~~~ 7/10/2018 ¦ i70604 ¦ Work Order(s) Generated
363 | Dist | Asheboro i25781 | ASHEBORO NORTH 115KV - ASHEBORO NORTH CENTRAL AVENUE 24KV | 7/6/2018 16:19 | 7/6/2018 16:56 | 4737148 | OCB - ABC FID: T0965B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | MP Porcelain | M2 Metering PT | A1 ABB |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 999 | 994 | 37 | Recloser~189A66_104817194 | Overhead Fac Overhead Switch / Recloser Failure Three Phase Recloser Failed RCL CAUGHT FIE | JWW///On 07/06/18 at 16:19 a PT on a G&W failed during a thunderstorm causing the Central Ave feeder to lock out and also A and C phase to lock out on another G&W (E336AD) on the Liberty Road feeder. When the service tech arrived he had DCC de-energize B phase on the Liberty Road feeder and then he took the normally open G&W off line and had DCC energize the Central Ave feeder and also the G&W on the Liberty Road restoring power to 999 customers on the Central Ave feeder and 926 customers on the Liberty Road G&W. ~~~ 7/9/2018 ¦ i25781 ¦ Work Order(s) Generated
364 | Dist | Raleigh e68825 | MORDECAI 115KV - CLEVELAND STREET 12KV | 7/7/2018 01:03 | 7/7/2018 01:22 | 4738727 | OCB - ABC FID: T5005B06 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | MA Aluminum | AS Sleeve, compression splice | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 920 | 1352 | 19 | Line~REM00_REM01_2850713 | Overhead Fac Overhead Primary Failure (No Tree Involved) Splice Failed In Line sleeve failed. at GIS# REM00 | PEEL 7/11/18: After Crew restored Outages 4738508 & 4738670, they heard fault sounds & saw flashes off in the distance. DCC advised C&M crew B-phase on the Cleveland St. feeder had dropped to 11 amps, C&M crew requested DCC to provide fault location, but they could not, and so had the C&M techs patrol the feeder from the substation until they found the culprit. The C&M tech finally found a #4 CU jumper connecting the tapline to XFMR bank had burned in two, and had contacted the feeder #477 line conductor at REM00, and somehow caused the splice to give way, dropping the B-phase conductor to the ground. Amazingly, there had been no fault to cause the FCB to open, and so the conductor portion which remained in place remained energized. To safely fix the issue, C&M techs decided they needed the feeder conductors de-energized, and so had DCC remotely open the Cleveland St. FCB. C&M repaired the line conductor and the tapline jumper, then had DCC remotely close the FCB to restore service. ~~~ 7/11/2018 ¦ e68825 ¦ Investigative Action
365 | Dist | Zebulon i70604 | BAILEY 230KV - BAILEY 23KV | 7/7/2018 07:58 | 7/7/2018 08:07 | 4739054-1 | OCB - ABC FID: T5450B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | MB Bronze | AB Air Break | SD S&C Electric |  | F2 Forced Outage | 00 Calm | 1115 | 1372 | 9 | Switch~ZLD46_1842828 | Overhead Fac Overhead Switch / Recloser Failure Air Break Switch Failed MIDDLE BLADE ON AIR BREAK SWITCH BURNT UP AT ZLD46 DROPPED REST OF THE FEEDER TO MAC OUT TEMP. MIDDLE BLADE ON AIR BREAK SWITCH BURNT UP AT ZLD46 DROPPED REST OF THE FEEDER TO MAC OUT TEMP. | CPS// Middle phase interrupter burned up on air break switch ZLD46 causing B phase customers down stream of switch to loss power (time and phase reflected in step 2). Responding line techs requested the circuit breaker to be opened so a temporary jumper could be installed (time and phases reflected in step 1). All customers were then restored. Equipment damaged was the Air Break switch. ~~~ 7/9/2018 ¦ i70604 ¦ Investigative Action
366 | Dist | Henderson i67431 | WARRENTON 115KV - WARRENTON INDUSTRIAL 23KV | 7/11/2018 07:23 | 7/11/2018 08:32 | 4741101 | RECLOSER - ABC FID: EA482_103384120 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 14 Closed Breaker | NA | UU Unknown Manufacturer | 0 | F2 Forced Outage | 00 Calm | 821 | 1247 | 69 |  | Overhead Fac Undetermined Recloser Lockout Under Hot Line Tag (Comments) switch under HLT ,no fault found switch under HLT ,no fault found | DPW: Recloser locked out under Hotlline tag. Cause could not be determined. Recloser EA482 was placed under Hotline Tag, Recloser EA265, the closest protective device to the work zone, was set in Sectionalizer Mode. Sectionalizer would not operate, it would only 'Count' ... EA482 would open up after one operation due to being on Hotline Tag. No photos available. ~~~ 7/11/2018 ¦ i67431 ¦ Investigative Action
367 | Dist | Cary JOCHRIS | MORRISVILLE 230KV - GATEWAY 23KV | 7/11/2018 15:53 | 7/11/2018 16:18 | 4741296-1 | OCB - ABC FID: T5010B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 00 Calm | 1155 | 1165 | 25 |  | Overhead Fac Undetermined FCB Lockout Under Hot Line Tag (Comments) CAUSE UNKNOWN AT THIS TIME CAUSE UNKNOWN AT THIS TIME | O. Christian - 7/13/2018 - Mastec Crew working installing poles in the span B990K-B991K were notified by DCC feeder had locked out. After interviewing the Line Foreman, he insisted that at the time DCC called him around 4:00pm that his crew was all in the clear and getting all equipment ready to end the days work. DCC informed foreman that feeder had locked out on Hot Line Tag. DCC was informed by Duke Energy line tech to try the breaker, breaker held and no problem was ever found. CYME put 2100 amp A-N fault at B990K-B991K location. No pictures and no evidence of flash/arcing found. ~~~ 7/13/2018 ¦ JOCHRIS ¦ Investigative Action
368 | Dist | Cary JOCHRIS | GREEN LEVEL 115KV - WILSONVILLE 24KV | 7/12/2018 12:56 | 7/12/2018 13:44 | 4741876-1 | OCB - ABC FID: T4603B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 1033 | 1403 | 48 | Line~456K_455K_2550042 | Human Interf OH - Vehicle None Dump truck hit cable line. | O. Christian - 7/13/2018 - Dump truck, with bed raised, proceeded to pull out on Hwy 64 East working on 36" diameter raw water pipe line, and snagged bottom joint use attachment (telephone) causing primary delta construction conductors to get together in span 456K-455K. Recloser at CCX82 failed to operate resulting in breaker opening. No mechanical damage to poles, insulators or conductors. No pictures. ~~~ 7/13/2018 ¦ JOCHRIS ¦ Investigative Action
369 | Dist | Durham dlm4375 | STALLINGS RD RET - 14282409 | 7/16/2018 12:07 | 7/16/2018 13:19 | 10828471 | S-RCL - ABC Size: 800 NVST FID: 358875359 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M8 Creosote | P1 Pole, Creosote | UU Unknown Manufacturer |  | F2 Forced Outage | 02 Rain | 831 | 2279 | 72 | BROKE POLE AT 1611 SHERRON RD | RECLOSER- SCADA SHERRON RD ONE POLE SOUTH OF HOLDER RD (1611) | dlm4375 recloser locked out due to vehicle at 1611 Sherron Rd.. had 50/3 creosote pole broke and ohvd tx on ground. the broke pole was floating by the overhead primary crew stabilized the pole and the crew cut the tap line and some secondary going across the road from the broke pole so the police could open the road and get the recloser back on..crew had to ,c/o 50/3 pole and install a 25 kva oh tx,14.4 back on new pole. ~~~ 7/17/2018 ¦ dlm4375 ¦ Investigative Action
370 | Dist | Chapel Hill AArias | HOMESTEAD - 19061208 | 7/16/2018 14:10 | 7/16/2018 18:17 | 10828957 | SolidBar - ABC Size: 300 Solid Bar FID: 39066508 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 56 Sectionalized/Restored Servic | 29 Conductor, bare | NA R |  | P4 Crew Initiated Outage | 00 Calm | 534 | 1322 | 247 | aarias// 7710 Rogers Rd | TL524/LANDERS OPENED SOLIDS TO GET PRIMARY BACK UP.. RELATED TO E 10828775.. | aarias// excavator tore A-ph of primary down. Ckt blinked once w/ AG fmag 2314 (tkt 10828744) and was still hot when crew got to site. Breaker opened (tkt 10828901) to isolate damage behind solid blades (tkt 10828957). Ckt had to be dropped again to re-energize solid blades (tkt 10829170) ~~~ 7/16/2018 ¦ AArias ¦ Investigative Action
371 | Dist | Chapel Hill AArias | HOMESTEAD - 19061208 | 7/16/2018 16:10 | 7/16/2018 16:24 | 10828901 | S-CKT - ABC Size: Class 2 FID: 38358777 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 14 Closed Breaker | 29 Conductor, bare | NA R |  | P4 Crew Initiated Outage | 00 Calm | 778 | 1322 | 14 | 7710 ROGERS RD | EMERG DROP ON CIRC.. COULD NOT LOAD BUST SOLIDS.. RELATED TO E 10828775.. | aarias// excavator tore A-ph of primary down. Ckt blinked once w/ AG fmag 2314 (tkt 10828744) and was still hot when crew got to site. Breaker opened (tkt 10828901) to isolate damage behind solid blades (tkt 10828957). Ckt had to be dropped again to re-energize solid blades (tkt 10829170) ~~~ 7/16/2018 ¦ AArias ¦ Investigative Action
372 | Dist | Chapel Hill AArias | HOMESTEAD - 19061208 | 7/16/2018 18:11 | 7/16/2018 18:17 | 10829170 | S-CKT - ABC Size: Class 2 FID: 38358777 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | 16 Accident, public vehicle | 14 Closed Breaker | 29 Conductor, bare | NA R |  | P4 Crew Initiated Outage | 00 Calm | 777 | 1322 | 6 | aarias// 7710 Rogers Rd |  | aarias// excavator tore A-ph of primary down. Ckt blinked once w/ AG fmag 2314 (tkt 10828744) and was still hot when crew got to site. Breaker opened (tkt 10828901) to isolate damage behind solid blades (tkt 10828957). Ckt had to be dropped again to re-energize solid blades (tkt 10829170) ~~~ 7/16/2018 ¦ AArias ¦ Investigative Action
373 | Dist | Raleigh e68825 | CHESTNUT HILLS 115KV - HICKORY HILLS 23KV | 7/22/2018 05:02 | 7/22/2018 07:12 | 4747751-1 | SWITCH - ABC FID: DQ56BK_1200555 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 56 Sectionalized/Restored Servic | P2 Pole, CCA | UU Unknown Manufacturer | 88 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1101 | 1600 | 130 | B294BK | Human Interf OH - Vehicle None CAR HIT POLE AT DIS#B294BK | Fontana 7/23/18 - Vehicle crashed into pole B294BK. Peel 7-23-18: Vehicle travelling westbound on East Millbrook Rd., apparently at a high rate of speed, lost control going around curve in the road at the Dantree Place intersection, hit and broke CCA pole B294BK, taking down two spans of feeder backbone, and locked out the FCB (driver fatality). Responding crews sectionalized the feeder backbone, isolated the downed section of feeder, restored service from other sources, made repairs to the feeder, then completed switching to restore the isolated section of feeder. ~~~ 7/23/2018 ¦ e68825 ¦ Investigative Action
374 | Dist | Asheboro i25781 | ASHEBORO WEST 115KV - UWHARRIE STREET 23KV | 7/22/2018 19:07 | 7/22/2018 20:19 | 4748312-2 | OCB - ABC FID: T0955B01 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | D4 Burned/Exploded | 43 Replaced Cutout and Fuse | 36 Cutout, fused | UU Unknown Manufacturer |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1276 | 2792 | 72 | 8815AD | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None Tree fell on 3phase breaking top of pole out at 8815AD. Also span of neutral down one pole up from it. Tree fell on 3phase breaking top of pole out at 8815AD. Also span of neutral down one pole up from it. | JWW// On 7/22/18 at 07:07pm a pine tree fell and broke pole causing 2788 customers to loose power. Self healing closed G&W 94G18 at 07:10pm restoring power to 1278 customers. When the Tech arrived he opened 3 cutouts at 9022AD. One of the cutouts was burnt up which is why the FDR locked out . He replaced the cutout and had DCC energize the feeder at 08:19pm restoring power to 1276 customers leaving 234 customers out until the pole was replaced. The remaining customers power was restored at 03:50am. ~~~ 8/1/2018 ¦ i25781 ¦ Investigative Action
375 | Dist | Cary JOCHRIS | MORRISVILLE 230KV - CARPENTER 23KV | 7/24/2018 10:10 | 7/24/2018 10:41 | 4749772 | RECLOSER - ABC FID: 181777_104603533 | 02 Line Recloser | OH Distribution Line Overhead | 28 Other Cause | 30 Error, Duke Contractor | 27 Other/See Notes | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 1227 | 2907 | 31 | Recloser~181777_104603533 | Human Interf OH - PE Contract Crew (Comments) PE Line Contractor Crew moving phases, got them together. | O. Christian - 10/3/2018 - Pike Electric working as a contractor for Duke Energy was replacing a pole at 4975K moving conductors in a delta construction span, when the line tech was moving an energized conductor attached at the jibe, when the jibe "wiggled" causing the middle and the road side phase to get together . The HLT tag on the recloser 181777 immediately locked out. Men and equipment placed in the clear, recloser closed and held. No damage to poles, conductors or line hardware. ~~~ 10/3/2018 (71 days) ¦ JOCHRIS ¦ Investigative Action
376 | Dist | Durham dlm4375 | ASHE STREET - 14021203 | 7/25/2018 12:03 | 7/25/2018 12:57 | 10841815 | S-CKT - ABC Size: Class 3 FID: 38355717 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | DK Disabled / by-passed | 56 Sectionalized/Restored Servic | CE Communications Duke | UU Unknown Manufacturer |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1578 | 2214 | 54 | dlm4375 800 Clayton Rd | TEER,ERIC IS ALSO ON 131 ON SITE LOCK OUT... FMAG 2066 AB TRIP 50, POSSIBLE FAULT LOCATION NEAR THE INTERSECTION OF CHEEK RD AND JUNCTION RD. 2806 CHEEK RD. CLOSED CIRCUIT AFTER ISOLATION USING 87234630 THERE IS A TREE AT 800 CLAYTON..JOHNNY MADE AWARE @1214 LEAD DESK CALLED @1215 | dlm4375...thunder storm in area... circuit out see 108421815 ..we had a defective tree fall 38' co-dominate stem defective at base of tree. Located 800blk of Clayton Rd which is behind a recloser facid 38998786 but the circuit went because the recloser was bypassed due to a bad modem. Crew opened 300 amp solid blade facid 87234630 see 10841926 to isolate and get circuit back on. After removing tree by tree crew our crew opened circuit again see 1042297 to close in solid blades. fu to GIS to fix annotation on solid blade ticket and also sent inquiry on the modem replacement. ~~~ 7/25/2018 ¦ dlm4375 ¦ Investigative Action
377 | Dist | Sanford i25781 | SANFORD HORNER BLVD. 230KV - GULF 23KV | 7/27/2018 21:37 | 7/27/2018 23:52 | 4751709 | OCB - ABC FID: T2440B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | MP Porcelain | 38 Insulator | UU Unknown Manufacturer |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1831 | 1839 | 135 | 6705AC | Broke 367R insulator at 6705AC | JWW// On 7/27/18 at 09:37pm during a strong thunder storm service tech responded to a feeder outage and found a broke 367R insulator at 6705AC. Tech replaced the insulator and had DCC energize the feeder at 11:52pm. The tech believed lighting struck the insulator causing it to break. ~~~ 7/31/2018 ¦ i25781 ¦ Investigative Action
378 | Dist | Raleigh DFontan | CHESTNUT HILLS 115KV - SANDY FORKS ROAD 23KV | 7/30/2018 14:38 | 7/30/2018 15:14 | 4754231 | RECLOSER - BC FID: 186A73_104703635 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 17 Tree error, public | 37 Removed Limb or Tree From Lin | NA | OA Oak |  | F2 Forced Outage | 00 Calm | 979 | 2196 | 36 | Load~C832BK | Human Interf Tree Cut on Line (By Logger or Customer) None TREE CREW CUT TREE ON LINE @ C832BK TREE CREW CUT TREE ON LINE @ C832BK | PEEL 7/31/18: Logger (public) cut an Oak tree limb into the feeder in span C832BL-C833BL, lodging into B&C phase conductors, locking out B&C phases of recloser 186A73. No damage. ~~~ 7/31/2018 ¦ DFontan ¦ Investigative Action
379 | Dist | Asheboro i25781 | ASHEBORO NORTH 115KV - ASHEBORO NORTH CENTRAL AVENUE 24KV | 7/30/2018 21:53 | 7/30/2018 22:27 | 4754427-2 | RECLOSER - ABC FID: 189A66_104817194 | 02 Line Recloser | OH Distribution Line Overhead |  | D4 Burned/Exploded | 41 Replaced Arrestor | A1 Arrester, polymer | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 524 | 994 | 34 | 12NX24 | Pole fire | JWW// On 7/30/18 at 09:53pm a poly lighting arrester failed causing a pole fire. When Tech arrived he had DCC drop FDR because he did not feel comfortable opening hook air break switch at G174AD. This lasted 6 minutes, after opening switch DCC energized the FDR back restoring power to 265 customers. Tech then went and opened air break switch at G345AD and had DCC energize the normally open G&W 189A66 at 10:27pm to restore power to 524 customers leaving 210 customers out while they replaced the pole. Power was restored at 03:25am ~~~ 8/6/2018 ¦ i25781 ¦ Investigative Action
380 | Dist | Selma i70604 | SELMA 230KV - MICRO 23KV | 7/31/2018 19:26 | 7/31/2018 20:08 | 4755253-1 | RECLOSER - ABC FID: 11Q013_104210001 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | M4 Composite | 48 Transformer | C7 Cooper |  | F2 Forced Outage | 00 Calm | 1115 | 2064 | 42 | Recloser~11Q013_104210001 | Overhead Fac Overhead Transformer Outage Partial/No Voltage | CPS// Lightning arrester failed to clear on a Y/ Delta transformer bank at Dis#UB37BA// The configuration was an old spec in which the lightning arrester was on the top side of the Fuse C/O for the transformer// The responding Service Tech removed the Riser and requested the DCC close G&W 11Q013// Damaged equipment included 2 C/O's, 1 transformer and 1 lightning arrester ~~~ 8/2/2018 ¦ i70604 ¦ Investigative Action
381 | Dist | Durham dlm4375 | GARRETT RD - 14202413 | 8/1/2018 00:02 | 8/1/2018 01:42 | 10848975 | S-CKT - ABC Size: Class 2 FID: 38355981 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | MP Porcelain | 38 Insulator | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 00 Calm | 5325 | 5339 | 100 | E WOODCROFT PKWY & FAYETTEVILLE | OPENED BREAKER TO PUT POLE TOP FIRE OUT...TEMP REPAIRS MADE UNTIL CREWS CAN WORK SOMETIME TODAY | aarias// opened FCB (tkt 10848975) to put pole top fire out at RCL 39008072 caused by defective C-ph bell insulator on North side. FCB open again (tkt 10852972) to open SBs (tkt 10852982) to temporarily brace top of pole with an 8 ft crossarm. FCB open again to close SBs (tkt 10853285). Recloser to remain offline until pole is replaced. Permanent repairs to be completed under WO 29356993 ~~~ 8/13/2018 ¦ dlm4375 ¦ Work Order(s) Generated
382 | Dist | Durham rlw2159 | DURHAM MAIN - 14011218 | 8/1/2018 14:02 | 8/1/2018 15:15 | 10849989 | S-CKT - ABC Size: Class 2 FID: 38355537 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 19 Lightning strike | 10 Vandalism | 39 Repaired Overhead Conductor | 29 Conductor, bare | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 2193 | 2200 | 73 |  | SPAN OF PRIMARY DOWN JUST OUTSIDE STATION PER UMBEHANT. DURHAM MAIN 1210 LOCKED OUT. "A" PHASE ON DURHAM MAIN 1218 LOCKED OUT. HAD TO OPEN 1218 BREAKER FOR REPAIRS. POSSIBLE LIGHTNING STRIKE ON SQUEEZE ON, PHASE FROM 1218 FELL ON ALL THREE PHASES OF 1210 | RLW-THE A PHASE ON 1218 BURNT TO THE GROUND AT A CONNECTION THAT APPEARS TO HAVE BEEN SHOT BY A GUN. THIS IS COMMON IN THIS AREA. THE A PHASE FELL ACROSS CKT 1210 CAUSING IT TO LOCK OUT ALSO. THAT TICKET# IS 10849822. THE PRIMARY WAS PUT BACK UP AND CIRCUIT RE-ENERGIZED. ~~~ 8/1/2018 ¦ rlw2159 ¦ Investigative Action
383 | Dist | Cary JOCHRIS | GREEN LEVEL 115KV - GREEN LEVEL 24KV | 8/1/2018 15:56 | 8/1/2018 16:53 | 4755799 | OCB - ABC FID: T4603B11 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | D4 Burned/Exploded | 54 Scheduled | 43 Recloser, Electronic | SD S&C Electric |  | F2 Forced Outage | 02 Rain | 3136 | 3251 | 57 | Switch~T4603B11 | Tree/Vegetatn Limb Fell from Outside Right of Way None | O. Christian - 8/8/2018 - PT cluster catastrophic failure setting fire to the G&W recloser at 17QL30. Work order 29378007 written to replace ASAP. ~~~ 8/8/2018 ¦ JOCHRIS ¦ Work Order(s) Generated
384 | Dist | Zebulon i70604 | WENDELL 230KV - LAKE GLAD ROAD 24KV | 8/2/2018 01:59 | 8/2/2018 02:35 | 4756018 | Switch - ABC FID: T5378B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead |  | 16 Accident, public vehicle | 47 Replaced Pole | P1 Pole, Creosote | UU Unknown Manufacturer |  | F2 Forced Outage | 02 Rain | 2260 | 2342 | 36 | Load~FU98BF |  | CPS// Public vehicle broke pole dis#FU98BF causing the Feeder Circuit Breaker to open. The responding service tech made the scene safe and asked the DCC to re-energize the circuit breaker. No pictures of old pole. No damage to wire but pole and transformer had to be replaced. ~~~ 8/3/2018 ¦ i70604 ¦ Investigative Action
385 | Dist | Cary JOCHRIS | AMBERLY 230KV - GREEN HOPE 24KV | 8/2/2018 14:11 | 8/2/2018 14:44 | 4756497-1 | OCB - ABC FID: T4604B19 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 2842 | 3010 | 33 |  | Overhead Fac Undetermined FCB Lockout Under Hot Line Tag (Comments) SUB MAINT WAS MOVING FROM TRANSF TO MAIN BREAKER WHEN IT LOCKED OUT RISSO | O. Christian - 8/6/2018 - Substation Maintenance was switching load from a temporary breaker to the Green Hope 23KV FDR with a HLT in place when something occurred to lock out the Green Hope 23KV FDR since it was on one shot. DCC gave the fault location as 139L62 which is a PME-9. Field Tech checked out the PME and found no problems. DCC instructed to test Green Hope 23KV FDR breaker and it held. No problems found and no pictures. ~~~ 8/6/2018 ¦ JOCHRIS ¦ Investigative Action
386 | Dist | Durham rlw2159 | GARRETT RD - 14202413 | 8/2/2018 17:53 | 8/2/2018 19:38 | 10852982 | SOH - ABC Size: 600 Line Disconnect FID: 39035152 | 08 Disconnect | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | MP Porcelain | 38 Insulator | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 00 Calm | 5090 | 5339 | 105 | reclosure pole at fayettville and woodcroft | circuit tripped to open fac id 39035152 due to RCL 34219094 pole on fire | aarias// opened FCB (tkt 10848975) to put pole top fire out at RCL 39008072 caused by defective C-ph bell insulator on North side. FCB open again (tkt 10852972) to open SBs (tkt 10852982) to temporarily brace top of pole with an 8 ft crossarm. FCB open again to close SBs (tkt 10853285). Recloser to remain offline until pole is replaced. Permanent repairs to be completed under WO 29356993 ~~~ 8/13/2018 ¦ rlw2159 ¦ Work Order(s) Generated
387 | Dist | Garner c72037 | RALEIGH WORTHDALE 230KV - GLENBROOK 23KV | 8/3/2018 10:33 | 8/3/2018 11:20 | 4757502-1 | OCB - ABC FID: T5168B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead |  | HT Unfused span(s) | DE Erosion/poor enviornment | 29 Conductor, bare | OR Oak, red | 40 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1587 | 1608 | 47 | FK71BJ |  | MHS- A defective oak tree broke about 15' above ground level and fell 40' from C/L burning all 3 phases down. Crew did a line cut at FK62BJ to hot the feeder back up and get 1587 customer on. they than opened fuses at dip pole FK73BJ, and back feed from FH75BJ to get the another 15 customers on the remaining 4 stayed out till work was completed. Crew installed cutouts at FK62BJ so this would not take out feeder again ~~~ 8/28/2018 (25 days) ¦ c72037 ¦ Investigative Action
388 | Dist | Zebulon i70604 | SPRING HOPE 115KV - SPRING HOPE 23KV | 8/4/2018 08:51 | 8/4/2018 09:01 | 4758326-1 | OCB - ABC FID: T6041B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | DG Fail to trip/interrupt | M8 Creosote | P1 Pole, Creosote | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 02 Rain | 1490 | 1807 | 10 |  | Overhead Fac Pole Failure Burned Pole caught on fire at HG51BC due to top phase coming off insulator laying against pole top pin, did not take out recloser ca Pole caught on fire at HG51BC due to top phase coming off insulator laying against pole top pin, did not take out recloser caused the pole to burn in half at the pole grounds for the capacitor bank. | CPS// Pole fire at dis#HG51BC due to conductor falling off of insulator// Reclosers at dis#HG31BC failed to open// Responding service tech requested that DCC open the feeder circuit breaker in order to clear fault (represented in step 1)// Crew replaced pole and re-energized remaining customers behind recloser dis# HG31BC (represented in step 2) Equipment damaged included pole, insulators, and insulator brackets ~~~ 8/6/2018 ¦ i70604 ¦ Investigative Action
389 | Dist | Cary JOCHRIS | APEX 230KV - APEX HIGHWAY 55 23KV | 8/6/2018 15:20 | 8/6/2018 15:36 | 4759993 | RECLOSER - XYZ FID: 9RK98_104607789 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 29 Permanent Repair | 44 Regulator |  |  | F2 Forced Outage | 00 Calm | 1914 | 2086 | 16 | Load~KG13 | Overhead Fac Distribution Line Regulator Regulator Problem/Failure (Comments) | O. Christian - 10/2/2018 - At regulator bank 18HX11, DCC stepped these regulators, which had been installed and bypassed for an extended period of time and had just been energized, causing two of the regulators to "birp" oil through the pressure relief valves. Regulators were then taken off line and will be replaced. Work order 29396171 has been written to replace all three regulators. ~~~ 10/2/2018 (57 days) ¦ JOCHRIS ¦ Investigative Action
390 | Dist | Garner omshistproc | GARNER TRYON HILLS 115KV - LOOP ROAD 24KV | 8/7/2018 04:39 | 8/7/2018 06:20 | 4760737-1 | OCB - ABC FID: T4720B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | 12 Lockout Without Perm Fault | 27 Other/See Notes | NA |  |  | F2 Forced Outage | 00 Calm | 531 | 1865 | 101 |  | Overhead Fac Undetermined Feeder Circuit Breaker Lockout | ... NO OUTAGE REVIEW INFO
391 | Dist | Selma i70604 | WILSON MILLS 230KV - GLENDALE 24KV | 8/7/2018 13:47 | 8/7/2018 14:12 | 4761045-1 | OCB - ABC FID: T5385B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M2 ACSR | 29 Conductor, bare | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 2418 | 1684 | 25 | Switch~T5385B02 | Human Interf OH - Vehicle None Lights on | CPS// Contract crew had a hot line tag on the feeder to replace some poles// During this time a public construction company made contact with energized conductor on a single phase tap line at dis#JP45BA causing a fuse to blow at dis#ZVQ81// The fault caused the breaker to open under hot line tag (represented in step 1)// The responding service tech identified the issue and asked DCC to re-energize the breaker// Repairs were made on the single phase line and all remaining customers were then restored (represented in step 2)// The only damage was to the Primary and neutral conductor at the Fault location// Tech repaired conductor with a splice ~~~ 8/9/2018 ¦ i70604 ¦ Investigative Action
392 | Dist | Raleigh DFontan | RALEIGH HOMESTEAD 230KV - GRESHAM LAKE 23KV | 8/7/2018 21:06 | 8/7/2018 23:33 | 4761387-3 | SWITCH - ABC FID: BM57BK_1192093 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 549 | 2357 | 147 | Span between pole 7MP95 and 512BK | Human Interf OH - Vehicle None BUCKET TRUCK IN LINE | Fontana 8/8/18 - A contractor for the DOT was facing south bound on US-1 just past Cheviot Hills Drive. The contractor was working on a street light and was in the bucket when he raised the boom into the neutral conductor which later contacted the bottom phase (A-phase). The A-phase primary burned to the ground and laid down across capital boulevard. The neutral was also melted and burned and a new neutral was put up. The span between poles 7MP95 and 512BK is where the line crosses from the north bound to south bound side of US-1 and is the span impacted. To perform the work Duke crew requested the Triangle Town feeder to be de-energized seeing it shares poles with the Gresham Lake feeder. Switch 6BT42 was opened and the FCB was closed to restore a number of customers. Soon after N.O. switches V442BK and BM57BK were closed. ~~~ 8/8/2018 ¦ DFontan ¦ Investigative Action
393 | Dist | Raleigh DFontan | RALEIGH HOMESTEAD 230KV - GRESHAM LAKE 23KV | 8/7/2018 21:06 | 8/7/2018 22:28 | 4761387-1 | OCB - ABC FID: T5125B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 752 | 2357 | 82 | Span between pole 7MP95 and 512BK | Human Interf OH - Vehicle None BUCKET TRUCK IN LINE | Fontana 8/8/18 - A contractor for the DOT was facing south bound on US-1 just past Cheviot Hills Drive. The contractor was working on a street light and was in the bucket when he raised the boom into the neutral conductor which later contacted the bottom phase (A-phase). The A-phase primary burned to the ground and laid down across capital boulevard. The neutral was also melted and burned and a new neutral was put up. The span between poles 7MP95 and 512BK is where the line crosses from the north bound to south bound side of US-1 and is the span impacted. To perform the work Duke crew requested the Triangle Town feeder to be de-energized seeing it shares poles with the Gresham Lake feeder. Switch 6BT42 was opened and the FCB was closed to restore a number of customers. Soon after N.O. switches V442BK and BM57BK were closed. ~~~ 8/8/2018 ¦ DFontan ¦ Investigative Action
394 | Dist | Raleigh DFontan | RALEIGH HOMESTEAD 230KV - GRESHAM LAKE 23KV | 8/7/2018 21:06 | 8/7/2018 23:02 | 4761387-2 | SWITCH - ABC FID: V442BK_1192050 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 937 | 2357 | 116 | Span between pole 7MP95 and 512BK | Human Interf OH - Vehicle None BUCKET TRUCK IN LINE | Fontana 8/8/18 - A contractor for the DOT was facing south bound on US-1 just past Cheviot Hills Drive. The contractor was working on a street light and was in the bucket when he raised the boom into the neutral conductor which later contacted the bottom phase (A-phase). The A-phase primary burned to the ground and laid down across capital boulevard. The neutral was also melted and burned and a new neutral was put up. The span between poles 7MP95 and 512BK is where the line crosses from the north bound to south bound side of US-1 and is the span impacted. To perform the work Duke crew requested the Triangle Town feeder to be de-energized seeing it shares poles with the Gresham Lake feeder. Switch 6BT42 was opened and the FCB was closed to restore a number of customers. Soon after N.O. switches V442BK and BM57BK were closed. ~~~ 8/8/2018 ¦ DFontan ¦ Investigative Action
395 | Dist | Raleigh DFontan | RALEIGH HOMESTEAD 230KV - TRIANGLE TOWN 24KV | 8/7/2018 21:45 | 8/8/2018 00:09 | 4761414 | OCB - ABC FID: T5125B11 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair | 29 Conductor, bare | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 00 Calm | 2168 | 127 | 144 | Node~26195849 | Human Interf OH - Vehicle None BUCKET TRUCK IN LINE | Fontana 8/8/18 - A contractor for the DOT was facing south bound on US-1 just past Cheviot Hills Drive. The contractor was working on a street light and was in the bucket when he raised the boom into the neutral conductor which later contacted the bottom phase (A-phase). The A-phase primary burned to the ground and laid down across capital boulevard. The neutral was also melted and burned and a new neutral was put up. The span between poles 7MP95 and 512BK is where the line crosses from the north bound to south bound side of US-1 and is the span impacted. To perform the work Duke crew requested the Triangle Town feeder to be de-energized seeing it shares poles with the Gresham Lake feeder. Switch 6BT42 was opened and the FCB was closed to restore a number of customers. Soon after N.O. switches V442BK and BM57BK were closed. ~~~ 11/12/2018 (96 days) ¦ DFontan ¦ Investigative Action
396 | Dist - MED | Chapel Hill AArias | HOMESTEAD - 19061209 | 8/8/2018 13:17 | 8/8/2018 14:16 | 10861924 | S-RCL - ABC Size: 560 WVE FID: 39005343 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 16 Closed Recl or Sectionalizer | PP Pole | NA R |  | F2 Forced Outage | 00 Calm | 586 | 1857 | 59 | 3000 EUBANKS RD | TL303 TO GET PIKE CREW....dump truck took wire and pole down, wire down across the road 3000 EUBANKS | aarias// dump truck took wire down and broke pole. Subdivision under construction in area, our facilities also undergoing upgrades. No permanent repairs necessary as this was an old pole and newly installed pole line was about to be energized ~~~ 8/13/2018 ¦ AArias ¦ Investigative Action
397 | Dist - MED | Durham rlw2159 | GREEN STREET - 14121209 | 8/8/2018 22:31 | 8/9/2018 00:42 | 10865030 | S-RCL - ABC Size: 560 WVE FID: 39009015 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 39 Repaired Overhead Conductor | 39 Disconnect | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 1278 | 2425 | 131 | CORNER OF CHAPEL HILL RD & MOREHEAD AVE | EMERGENCY DROP ON RECLOSER DUE TO IN LINE BURNING UP, WILL NEED TO BYPASS. replaced inline disconnect no follow up needed, HANK TAYLOR & AL HOWARD | rlw-storm in area-EMERGENCY DROP ON RECLOSER DUE TO IN LINE BURNING UP, WILL NEED TO BYPASS. replaced inline disconnect no follow up needed ~~~ 8/15/2018 ¦ rlw2159 ¦ Investigative Action
398 | Dist | Zebulon i70604 | ROLESVILLE 230KV - ROLESVILLE 24KV | 8/11/2018 19:59 | 8/11/2018 20:08 | 4766120 | OCB - ABC FID: T5205B12 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | MP Porcelain | 38 Insulator | UU Unknown Manufacturer |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 2064 | 2160 | 9 | Line~CG58CA_CG60CA_1415279 | Overhead Fac Overhead Primary Failure (No Tree Involved) Conductor Broke/Burned Down wire fell on crossarm at J832BF crews on site for the repair | CPS// Major T-Storm// Round base insulators broke at dis#J832BF causing circuit breaker to open// Responding service tech opened air break switch 17PG69 isolating fault// DCC closed breaker (Reflected in Out#4766120)// Crews made repairs and restored remaining customers behind 17PG69 (Reflected in Out#4766132)// Damage to equipment was two round base insulators ~~~ 8/14/2018 ¦ i70604 ¦ Investigative Action
399 | Dist | Zebulon i70604 | NASHVILLE 115KV - CORINTH 23KV | 8/12/2018 11:02 | 8/12/2018 11:57 | 4766779 | OCB - ABC FID: T5900B05 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | HW Mid Span Fault | 14 Closed Breaker | NA | SZ Sweet Gum |  | F2 Forced Outage | 00 Calm | 1834 | 1850 | 55 | Line~BD56BC_BD58BC_1940611 | Tree/Vegetatn Limb Fell from Inside Right of Way None limb fell on primary | CPS// Sweet gum limb fell from established overhang at dis#BD56BC causing a mid span fault up stream of G&W A815BC. Responding Line Tech removed limb and asked DCC to close the Breaker. Ran fault current using FMS & CYME but was unable to identify exact location in the field of the mid span fault (no visible wire pitting or burn marks). No damage to equipment. Could not measure distance from wire to where limb broke out of tree. ~~~ 8/14/2018 ¦ i70604 ¦ Investigative Action
400 | Dist | Asheboro i25781 | BISCOE 115KV - BISCOE 23KV | 8/13/2018 07:59 | 8/13/2018 09:11 | 4767817-1 | OCB - ABC FID: T0990B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 29 Permanent Repair | 43 Recloser, Electronic | A1 ABB |  | F2 Forced Outage | 00 Calm | 556 | 561 | 72 | Recloser~17YP75_105656960 | Overhead Fac Overhead Switch / Recloser Failure Three Phase Recloser Failed IPP RECLOSER BURNT UP AT 17YP75 | JWW// On 8/13/18 at 07:59am G&W at 17YP75 that feeds an IPP customer failed locking out the Biscoe feeder causing 556 people to lose power. When Tech arrived he cleared the G&W and had DCC energize the feeder restoring power to 556 customers. This was the G&W that failed not the PT cluster. An order has been written to replace the G&W. ~~~ 8/14/2018 ¦ i25781 ¦ Work Order(s) Generated
401 | Dist | Roxboro i67431 | BAHAMA 230KV - ROUGEMONT 23KV | 8/14/2018 13:16 | 8/14/2018 14:08 | 4769183-2 | RECLOSER - ABC FID: E0C13_104887891 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | FD R Fault on Transmission Line | DD Co-dominate stem | P2 Pole, CCA | OA Oak | 25 | F2 Forced Outage | 00 Calm | 830 | 1906 | 52 | Switch~T4555B01 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None broken pole broken pole | DPW: Diseased Oak tree falls at E1235, breaking pole and locking out the Rougemont Feeder. E1217(630A OVR) was opened, ABS 11G058 was opened to deenergize fault location. Recloser E0C13 was closed in to tie in the Durham Rd Feeder, leaving approximately 216 customers off, and an IPP customer(2). Pole was replaced and repairs made. ~~~ 8/17/2018 ¦ i67431 ¦ Investigative Action
402 | Dist | Roxboro i67431 | BAHAMA 230KV - ROUGEMONT 23KV | 8/14/2018 13:16 | 8/14/2018 14:03 | 4769183-1 | OCB - ABC FID: T4555B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | FD R Fault on Transmission Line | DD Co-dominate stem | P2 Pole, CCA | OA Oak | 25 | F2 Forced Outage | 00 Calm | 860 | 1906 | 47 | Switch~T4555B01 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None broken pole broken pole | DPW: Diseased Oak tree falls at E1235, breaking pole and locking out the Rougemont Feeder. E1217(630A OVR) was opened, ABS 11G058 was opened to deenergize fault location. Recloser E0C13 was closed in to tie in the Durham Rd Feeder, leaving approximately 216 customers off, and an IPP customer(2). Pole was replaced and repairs made. ~~~ 8/17/2018 ¦ i67431 ¦ Investigative Action
403 | Dist | Zebulon i70604 | NASHVILLE 115KV - NASHVILLE 23KV | 8/14/2018 14:28 | 8/14/2018 14:56 | 4769251-1 | OCB - ABC FID: T5900B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | DG Fail to trip/interrupt | MA Aluminum | 10 Sectionalizer | SD S&C Electric |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1500 | 1608 | 28 | 7K394 | Tree/Vegetatn Tree Outside Right of Way (Fall/Lean On Primary) None respliced wire | CPS// Single phase sectionalizer failed to open at dis#7K391 causing feeder circuit breaker to open // Line techs opened sectionalizer to isolate fault (Reflected in step 1)//Fault was located at dis#7K394 wire burned down, believed to be caused by lightning // Wire was repaired and remaining customers were restored (Reflected in step 2) // Damage to equipment was #2ACSR conductor ~~~ 8/17/2018 ¦ i70604 ¦ Investigative Action
404 | Dist | Selma i70604 | WILSON MILLS 230KV - WEST SMITHFIELD 24KV | 8/18/2018 23:05 | 8/19/2018 05:43 | 4774140-2 | SWITCH - ABC FID: JQ32BA_1717632 | 08 Disconnect | OH Distribution Line Overhead | 11 Unknown Cause | 20 Equipment failure | M4 Composite | 38 Insulator | PX PBI |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1762 | 1867 | 398 | NJ87BA | Overhead Fac Undetermined Feeder Circuit Breaker Lockout EQUIPMENT FAILURE AT NJ87BA | CPS// MV sensors at dis#NJ87BA failed causing 477 conductor to burn down// Responding service tech opened air break switch JQ32BA to isolate fault (Reflected in step 1)// Repairs were made to conductor and new insulators were installed then all remaining customers were restored (Reflected in step 2)// Damage to equipment included MV sensors and 477 conductor// Note: A contract crew was dispatched from Greensboro to make repairs ~~~ 8/21/2018 ¦ i70604 ¦ Investigative Action
405 | Dist | Cary JOCHRIS | RTP 230KV - MCCRIMMON 24KV | 8/19/2018 10:11 | 8/19/2018 10:40 | 4774733 | SWITCH - ABC FID: 51K04_2667578 | 08 Disconnect | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 29 Permanent Repair | AB Air Break | SD S&C Electric |  | F2 Forced Outage | 00 Calm | 528 | 1466 | 29 | Switch~51K04_2667578 | Overhead Fac Overhead Switch / Recloser Failure Air Break Switch Failed 51K04 | O. Christian - 10/2/2018 - Top phase of vertical ABS 51K04 was not making good connection in the closed position and was arching upon line tech's arrival. Proceeded to have DCC open breaker so that vertical ABS 51K04 could be opened to isolate switch and to close ABS 15QH23 to backfeed and get customers back on as soon as possible. Work order 29522873 written to replace defective vertical ABS at 51K04. ~~~ 10/2/2018 (44 days) ¦ JOCHRIS ¦ Investigative Action
406 | Dist | Garner c72037 | FUQUAY 230KV - FUQUAY SOUTH PARK 23KV | 8/21/2018 09:33 | 8/21/2018 13:15 | 4776811 | OCB - ABC FID: T4710B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | HT Unfused span(s) | DC Internal stem decay | 29 Conductor, bare | OA Oak | 35 | F2 Forced Outage | 00 Calm | 3375 | 3385 | 222 | F068BH | Tree/Vegetatn Limb Fell from Outside Right of Way None Tree fell at F068BH knocking down 3 spans of #2 wire. | MHS- crew had a defective Oak tree about 16" in DIA. fall from ground level and about 35' from C/L taking down all 3 phases of #2 Primary at DIS# F068BH. crew did a line cut at F056BH and got the feeder back hot getting 3,221 customers back on. While crews worked to repair primary, another crew installed cutouts at F056BH. ~~~ 8/28/2018 ¦ c72037 ¦ Investigative Action
407 | Dist | Durham rlw2159 | DACIAN AVEN - 14132409 | 8/22/2018 12:16 | 8/22/2018 12:48 | 10879613 | S-CKT - ABC Size: Class EX FID: 38356401 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | HR Reclose Block, fault occurred | MP Porcelain | 38 Insulator | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 642 | 644 | 32 | 2 POLES OUTSIDE OF SUBSTATION | FMAG 4143 Targets BG TCC called due to high fault MAG CHRIS HOOFT HAS BLOCK,IS RIDING OUT. WILL CALL, per Chri hooft circuit was out due to bad insulator, repaired insulator and returned circuit back to normal | rlw2159-crew had circuit blocked and was tying wire in on new insulator. Per/Kevin Shambley crew had all rubber required on arm and insulator, while crew was tying wire in on insulator the insulator broke down causing the circuit to lock out. Duke(Rick Canavan)has possession of the insulator. ~~~ 8/23/2018 ¦ rlw2159 ¦ Investigative Action
408 | Dist | Durham rlw2159 | DURHAM MAIN - 14011204 | 8/22/2018 16:46 | 8/22/2018 18:19 | 10879964 | S-CKT - ABC Size: Class 3 FID: 38355249 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 00 Calm | 1079 | 1082 | 93 | liberty and peachtree. balloons on line | CMPL 2018-08-22 18:20:00 by LEMCKIN RMK: LOCKOUT...TARGET BC FMAG 2986 HALO ON N DILLARD ST FROM LIBERTY ST TO S ROXBORO ...PRIORITY AT 410 LIBERTY ST BALLON ON LINE CAUSED SPARKS | rlw2159-ci4rcuit was blocked--balloons got into primary at Liberty and Peachtree streets and locked the circuit out. No burn marks or evidence of them on wire per line tech due to circuit being locked out. ~~~ 8/23/2018 ¦ rlw2159 ¦ Investigative Action
409 | Dist | Raleigh DFontan | LEESVILLE WOOD VALLEY 230KV - WOOD VALLEY 24KV | 8/22/2018 17:37 | 8/22/2018 18:27 | 4778062-1 | RECLOSER - BC FID: LM53BL_103935523 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA |  |  | F2 Forced Outage | 00 Calm | 610 | 1615 | 50 |  | Overhead Fac Undetermined Recloser Lockout | Fontana 8/24/18 - Recloser locked out and C&M responder did not find anything. After performing a CYME analysis we determined there was an AC phase fault predicted to be between spans 158343 and KX82BL. After a thorough foot patrol along the predicted fault location we found nothing and expanded our search a few spans further. We found a dead branch fragment hanging on the neutral between span KX80BL to JX79BL. However, we were not able to definitely say that branch caused the outage as it was exceptionally small and probably not large enough to cause the outage depicted by FMS. ~~~ 8/24/2018 ¦ DFontan ¦ Investigative Action
410 | Dist | Zebulon i70604 | ZEBULON 115KV - ZEBULON WEST 23KV | 8/22/2018 18:16 | 8/22/2018 19:58 | 4778105-1 | OCB - ABC FID: T5205B02 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | HT Unfused span(s) | DN No apparent defect | NA | SZ Sweet Gum |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 659 Cust Eq: 1234 | 1946 | 102 | C563BF | Tree/Vegetatn Limb Fell from Inside Right of Way None TREE ON TAP LINE AND BURNED DOWN PRIMARY THAT WAS SQUEEZED TO FEEDER WITHOUT A FUSE. TREE ON TAP LINE AND BURNED DOWN PRIMARY THAT WAS SQUEEZED TO FEEDER WITHOUT A FUSE. | CPS// Sweet gum limb broke and fell from outside of R/W on single phase tap at dis#C563BF // Tap line was not fused, causing circuit breaker to open // Self Healing team operated correctly restoring customers back to G&W C629BF (Reflected in step 1) // Line techs isolated the tap and DCC closed the feeder circuit breaker (Reflected in step 2) // Tree limb was removed and while crew was on site a 50KS fuse was installed on take off pole 159H09 (Reflected in step 3)// No damage to equipment and SR 1992611 was created to correct GIS ~~~ 8/24/2018 ¦ i70604 ¦ Investigative Action
411 | Dist | Garner c72037 | RALEIGH WORTHDALE 230KV - GLENBROOK 23KV | 8/24/2018 11:11 | 8/24/2018 11:27 | 4779577-1 | RECLOSER - ABC FID: DG24BJ_104176315 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair | P2 Pole, CCA | NA R | 0 | F2 Forced Outage | 00 Calm | 729 | 1608 | 16 | Node~1838950 | Human Interf OH - Vehicle None CAR HIT POLE, REPLACING | MHS- A car left the road and hit pole AF97BJ, breaking pole about 3' above ground level the fault opened up recloser DG24BJ. the crew opened up A/B Switch AG09BJ and closed back in recloser DG24BJ getting 729 customers back on. when crew had finished replacing pole, crew closed A/B Switch AG09BJ back in getting the remaining 42 customers back on ~~~ 8/28/2018 ¦ c72037 ¦ Investigative Action
412 | Dist | Durham rlw2159 | DURHAM MAIN - 14011216 | 8/26/2018 08:48 | 8/26/2018 10:47 | 10882481 | S-CKT - ABC Size: Class 1A FID: 38355525 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | 25 Improper Installation | MA Aluminum | 73 Compression | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 2078 | 2212 | 119 | n duke and dacian ave | CMPL 2018-08-26 11:09:00 by BJACOBY RMK: LOCKOUT - LINES BURNT DOWN JUST OUTSIDE OF THE STATION - N DUKE ST AND DACIAN AVE | rlw2159-span of wire burned down at n duke and dacian ave due to aluminum jumper being squeezed on copper main line instead of tail out of dead end shoe causing wire to burn down. This also caused blink on outage ID# 10882478. ~~~ 8/27/2018 ¦ rlw2159 ¦ Investigative Action
413 | Dist | Durham rlw2159 | ASHE STREET - 14021208 | 8/27/2018 12:38 | 8/27/2018 20:49 | 10883205 | FOH - ABC Size: 80 T FID: 38805980 | 03 Line Fuse | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 44 Replaced Fuse | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 503 | 2247 | 491 |  | truck took down lines...poss broke pole related to E#10883225 LINES DOWN - PUT LINES UP BACK ON PER BRIAN PRUITT | rlw2159-broken pole, primary down due t vehicle accident. Crew put primary back up and refused-pole to be changed out at a later date. This caused the blink on ticket# 10883203 ~~~ 8/28/2018 ¦ rlw2159 ¦ Work Order(s) Generated
414 | Dist | Raleigh DFontan | PINE LAKE 230KV - HIGHWAY 401 24KV | 8/29/2018 08:40 | 8/29/2018 08:58 | 4782980-1 | RECLOSER - ABC FID: 1CPC55_114387191 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 16 Closed Recl or Sectionalizer | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 577 Cust Eq: 196 | 1584 | 18 | BJ48BK | Human Interf OH - Vehicle None POLE HIT AT DIS#BJ48BK | Fontana 8/30/18 - A vehicle traveling south on Louisburg Road jumped the curb and smashed into pole BJ48BK. Pole has very minor damage mostly consisting of paint marks and scuffs. No repairs made. Pole is about 24 feet off the closest lane of traffic. The impact of the vehicle shook and pole and caused the lines to slap together causing the recloser to lock out. ~~~ 8/30/2018 ¦ DFontan ¦ Investigative Action
415 | Dist | Zebulon i70604 | WENDELL 230KV - WENDELL HIGHWAY 64 24KV | 8/30/2018 09:55 | 8/30/2018 12:00 | 4783891 | RECLOSER - BC FID: E861BF_103921648 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | MN Salt | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 1081 | 2791 | 125 | Line~E862BF_E866BF_1728424 | Human Interf OH - Vehicle None CAR HIT POLE AT E862BF | CPS// Public vehicle broke pole dis#E862BF causing B&C phase to open at G&W E861BF (step 1 reflected in out#4783891) // Due to public safety concerning the driver of the public vehicle DCC opened A phase on G&W E861BF (step 1 reflected in out#4783893) // Switching was performed by Line Techs to restore customers up to disconnects at 17H576 (reflected in step 1 & 2) // Pole was replaced and remaining customers restored ( step 3 reflected in out# 4784014) // Damage to equipment included broken pole, insulators, and damaged 25KVA OH Trans ~~~ 9/4/2018 ¦ i70604 ¦ Investigative Action
416 | Dist | Zebulon i70604 | WENDELL 230KV - WENDELL HIGHWAY 64 24KV | 8/30/2018 10:07 | 8/30/2018 12:00 | 4783893 | RECLOSER - A FID: E861BF_103921648 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | MN Salt | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 627 | 2791 | 113 | E862BF | Human Interf OH - Vehicle None CAR HIT POLE AT E862BF | CPS// Public vehicle broke pole dis#E862BF causing B&C phase to open at G&W E861BF (step 1 reflected in out#4783891) // Due to public safety concerning the driver of the public vehicle DCC opened A phase on G&W E861BF (step 1 reflected in out#4783893) // Switching was performed by Line Techs to restore customers up to disconnects at 17H576 (reflected in step 1 & 2) // Pole was replaced and remaining customers restored ( step 3 reflected in out# 4784014) // Damage to equipment included broken pole, insulators, and damaged 25KVA OH Trans ~~~ 9/4/2018 ¦ i70604 ¦ Investigative Action
417 | Dist | Raleigh DFontan | RALEIGH LEESVILLE ROAD 230KV - OAK PARK 23KV | 8/30/2018 11:30 | 8/30/2018 11:52 | 4783932-1 | OCB - ABC FID: T4910B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | 30 Error, Duke Contractor | 37 Removed Limb or Tree From Lin |  |  |  | F2 Forced Outage | 00 Calm | 1477 | 1478 | 22 | L0304 | Human Interf OH - PE Crew (Comments) None TREE CREW GOT TREE INTO LINE | Fontana 8/31/18 - A Duke Energy contractor (Burford Trees) were trimming the oak forest feeder. The crew was near pole L0304 when they sawed off a 54 inch limb from an approximately 65 foot tall Virginia pine located about 8 feet off the feeder center line. The limb contacted A and C phases and locked out the FCB. The responding C&M serviceman quickly arrived on scene and told DCC to close the breaker back in. No repairs made and no damage to our facilities. ~~~ 8/31/2018 ¦ DFontan ¦ Investigative Action
418 | Dist | Henderson i67431 | OXFORD NORTH 230KV - ORPHANAGE 23KV | 8/30/2018 19:42 | 8/31/2018 00:31 | 4784652 | OCB - ABC FID: T5090B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 29 Permanent Repair | AB Air Break |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 1586 | 1584 | 289 | Switch~EU774_1199130 | Overhead Fac Overhead Switch / Recloser Failure Air Break Switch Failed EU774-Will need to be replaced / | DPW: Service tech attributes ABS failure to a lightning strike, ABS was replaced. ~~~ 9/4/2018 ¦ i67431 ¦ Work Order(s) Generated
419 | Dist | Henderson omshistproc | HENDERSON NORTH 115KV - GREYSTONE 23KV | 8/30/2018 20:48 | 8/31/2018 01:18 | 4784492 | RECLOSER - ABC FID: E6L25_104601260 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 567 | 1438 | 270 | Line~10CB77_EKA15_1772211 | Overhead Fac Undetermined Recloser Lockout wire down PRIMARY DOWN AT GRETA LN WIRE DOWN AT 10CB77- EKA15 TREE FELL OUTSIDE ROW | ... NO OUTAGE REVIEW INFO
420 | Dist | Asheboro i14740 | TROY BURNETTE STREET 115KV - BILHEN STREET 13kV | 8/31/2018 03:53 | 8/31/2018 04:07 | 4785357 | OCB - ABC FID: T1612B11 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | 19 Lightning strike | M3 Copper | 74 Wire, copper | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 04 Wind, Rain and Lightning | 517 | 524 | 14 | 4518 | Overhead Fac Overhead Connections / Jumper Failure Jumper Burned In Two CUT OUT JUMPER BURNT IN TO AT 4518 | Lightning struck top of pole and burned copper jumper in two on the cutout for a tap line. Once the service man arrived he found the bottom side of the jumper to the tap line hanging just a few inches from another phase. Due to the winds from the storm he had DCC to open up the OCB long enough for him to place grounds, make repairs to the jumper, and then remove grounds. This resulted in a 14 minute outage for 517 customers. Verified time off through FMS. BDH ~~~ 9/10/2018 ¦ i14740 ¦ Investigative Action
421 | Dist | Raleigh DFontan | RALEIGH FOXCROFT 230KV - SOUTH HALL 23KV | 9/3/2018 03:40 | 9/3/2018 04:49 | 4787273-2 | SWITCH - ABC FID: 5WF11_1200534 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 1704 | 2742 | 69 | 100G22 | Human Interf OH - Vehicle None car hit pole at 100G22 | FONTANA 9/4/18 - A vehicle was traveling south of Southall Road when the driver lost control around a sharp turn, went offroad and hit pole 100G22. Crews had to replace the pole as well as perform some switching. They closed the switch in compartment 1 of 5WF11 and closed the N.O. point at 10GE45. ~~~ 9/4/2018 ¦ DFontan ¦ Investigative Action
422 | Dist | Raleigh DFontan | RALEIGH FOXCROFT 230KV - SOUTH HALL 23KV | 9/3/2018 03:40 | 9/3/2018 04:35 | 4787273-1 | OCB - ABC FID: T4692B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 1000 | 2742 | 55 | 100G22 | Human Interf OH - Vehicle None car hit pole at 100G22 | FONTANA 9/4/18 - A vehicle was traveling south on Southall Road when the driver lost control around a sharp turn, went offroad and hit pole 100G22. Crews had to replace the pole as well as perform some switching. They closed the switch in compartment 1 of 5WF11 and closed the N.O. point at 10GE45. ~~~ 9/4/2018 ¦ DFontan ¦ Investigative Action
423 | Dist | Garner c72037 | FUQUAY 230KV - PURFOY ROAD 23KV | 9/5/2018 14:50 | 9/5/2018 15:25 | 4789421 | SWITCH - ABC FID: GNC03_2636498 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA | NA R | 0 | F2 Forced Outage | 00 Calm | 1505 | 1610 | 35 | GCN15 | Human Interf OH - Vehicle None CAR HIT POLE AT CGN15 | MHS- A car left the road and hit pole DIS# GCN15 breaking it at ground level, locking out the Purfoy Road. FCB. crew opened up air break switch GNC03 then had DCC reenergize the FCB. Crew than replaced pole ,closing in switch when work was complete ~~~ 10/24/2018 (49 days) ¦ c72037 ¦ Investigative Action
424 | Dist | Henderson i67431 | LOUISBURG 115KV - INGLESIDE 23KV | 9/5/2018 15:56 | 9/5/2018 19:50 | 4789670 | RECLOSER - XYZ FID: 1C8F81_112849478 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 17 Tree error, public | 39 Repaired Overhead Conductor | 29 Conductor, bare | HW HARDWOOD |  | F2 Forced Outage | 00 Calm | 1015 | 1381 | 234 | EDV84-EDV85 | Human Interf Tree Cut on Line (By Logger or Customer) None line damaged by construction crew line damaged by construction crew | DPW: Tree cut by crew took down neutral. Before neutral could be reinstalled on pole, construction crew hung neutral and pulled off pole and taking primary down with it, locking out recloser 1C8F81. There is also a damage billing investigation.(memo to file outage 4789620, 2 minute difference,... according to IEEE this was not outage) ~~~ 9/6/2018 ¦ i67431 ¦ Work Order(s) Generated
425 | Dist | Cary JOCHRIS | GREEN LEVEL 115KV - WILSONVILLE 24KV | 9/6/2018 15:48 | 9/6/2018 16:46 | 4790485-1 | SWITCH - ABC FID: CAD92_103607422 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 17 Tree error, public | 37 Removed Limb or Tree From Lin | 29 Conductor, bare | PW Pine, white | 32 | F2 Forced Outage | 00 Calm | 1243 | 1403 | 58 | Line~CC437_CC436_2551062 | Human Interf Tree Cut on Line (By Logger or Customer) None | O. Christian - 9/27/2018 - Clearing Contractor clearing Right of Way for 36" raw water line installation coming from Jordan Lake and headed east to Cary, felled 16" diameter live white pine tree 32' from CL. Tree removed from line and service restored. No mechanical damage to poles, conductor or distribution equipment. Outage time of 57 minutes. ~~~ 9/27/2018 (21 days) ¦ JOCHRIS ¦ Investigative Action
426 | Dist | Henderson i67431 | WARRENTON 115KV - NORLINA 23KV | 9/8/2018 01:14 | 9/8/2018 01:26 | 4791619 | SWITCH - ABC FID: EA257_103467724 | 08 Disconnect | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 29 Permanent Repair | 43 Recloser, Electronic |  |  | F2 Forced Outage | 00 Calm | 587 | 1703 | 12 | Recloser~157R19_103368444 | Overhead Fac Overhead Switch / Recloser Failure Three Phase Recloser Failed Opened switch to clear blown PT | DPW: Service Tech received 911 ticket, pole on fire (157R19). Recloser did not lock out. PT cluster failed on Recloser 157R19, opened switch EA257 to clear PT on recloser. Potential Transformer has been replaced. ~~~ 9/10/2018 ¦ i67431 ¦ Investigative Action
427 | Dist | Zebulon i70604 | ZEBULON 115KV - WAKEFIELD STREET 23KV | 9/8/2018 06:22 | 9/8/2018 07:14 | 4791857-1 | OCB - ABC FID: T6090B10 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | HT Unfused span(s) | MS Steel | G1 Guywire | NA R |  | F2 Forced Outage | 00 Calm | 1825 | 1838 | 52 | Node~1552321 dis#5HZ52 | Human Interf OH - Vehicle None AY31BF - AY12BF | CPS// Public vehicle struck guy wire at dis#5HZ52 causing guy wire to break// Primary conductor slapped together causing circuit breaker to open// One span three phase tap was not fused// Damage included broken guy wire// Responding Service Tech repaired guy and service was restored// WR#29811089 Created to install fuses on AY31BF ~~~ 9/11/2018 ¦ i70604 ¦ Investigative Action
428 | Dist | Garner c72037 | CLAYTON 115KV - BARBER MILL 24KV | 9/10/2018 07:52 | 9/10/2018 08:53 | 4795279-1 | RECLOSER - ABC FID: NE84BJ_104125198 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | M8 Creosote | P1 Pole, Creosote | NA R | 0 | F2 Forced Outage | 00 Calm | 1821 | 2523 | 61 | 11AH21_ | Overhead Fac Pole Failure Burned Pole changed, system back to normal. | MHS- Dip riser at DIS# 11AH22 caught fire and burnt top of pole locking out recloser at NE84BJ. When crew arrived they did some switching first they went to A/B switch 5KY82 and opened it up then closed the recloser at NE84BJ getting 1821 customers back on. Next they open A/B switch 12FG55 and closed recloser 12FG60 tying the Cornwallis to the Barbour mill, then the crew did a line cut at DIS# 9X060. after that they closed in A/B switch 5KY82. Getting all but 356 customers back on till the pole was replaced. didn't get pics on this one. but crew said the fire started at dip riser. ~~~ 9/26/2018 (16 days) ¦ c72037 ¦ Investigative Action
429 | Dist | Henderson i40607 | HENDERSON NORTH 115KV - HENDERSON N INDUSTRIAL 23KV | 9/11/2018 11:57 | 9/11/2018 12:06 | 4796503 | OCB - ABC FID: T4770B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 00 Calm | 1370 | 1375 | 9 | Line~EJV39_EKS45_1747534 | Overhead Fac Undetermined FCB Lockout Under Hot Line Tag (Comments) contractor got wires together | Contractor working at replacing pole EKS45 got jib into covered conductor which caused 2 phases to make contact down span Tight construction. Circuit was on HLT and opened under one shot. ~~~ 9/12/2018 ¦ i40607 ¦ Completion Codes or Remarks
430 | Dist | Garner c72037 | GARNER I-40 230KV - NEW HOPE 24KV | 9/11/2018 21:54 | 9/11/2018 22:02 | 4796917 | OCB - ABC FID: T4723B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 05 Planned (IEEE) | D1 Broken/Malfunctioning | M3 Copper | 74 Wire, copper | NA R | 0 | P4 Crew Initiated Outage | 00 Calm | 2625 | 2767 | 8 | EJ64BJ | Planned Outage OH - Repair/Replace Damaged or Failed Facilities Other - OH BAD TX BUSHING WIRE HANGING | MHS-crew arrived to find transformer riser hanging having burnt loose from the bushing at the bend, crew had DCC drop the FCB while they replaced the riser, then they had DCC hot the FCB back up ~~~ 9/28/2018 (17 days) ¦ c72037 ¦ Investigative Action
431 | Dist - MED | Sanford omshistproc | SANFORD HORNER BLVD. 230KV - GULF 23KV | 9/13/2018 10:40 | 9/13/2018 11:49 | 4798289 | RECLOSER - BC FID: 17BJ98_104130120 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA |  |  | F2 Forced Outage | 00 Calm | 806 | 1839 | 69 |  | Overhead Fac Undetermined Recloser Lockout PATROLLED AND NOTHING FOUND nothing found | ... NO OUTAGE REVIEW INFO
432 | Dist - MED | Henderson i40607 | WARRENTON 115KV - WARRENTON INDUSTRIAL 23KV | 9/13/2018 22:44 | 9/14/2018 00:45 | 4818744 | RECLOSER - ABC FID: EA265_112850461 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 22 Inadequate Clearances | 16 Closed Recl or Sectionalizer | NA |  |  | F2 Forced Outage | 12 Hurricane | 823 | 1247 | 121 | ECF04 | Overhead Fac Undetermined Recloser Lockout UNKNOWN | G&W Recloser EA265 locked out because conductor laid out for reconductoring and phase were slapping together due to wind between ECF04-ECF32 ~~~ 9/16/2018 ¦ i40607 ¦ Completion Codes or Remarks
433 | Dist - MED35 | Selma omshistproc | FOUR OAKS 230KV - HANNAHS CREEK 24KV | 9/14/2018 00:23 | 9/14/2018 16:21 | 4823200 | LINE CUT - AB FID: Line Cut-609898 | 09 Jumper/wire cut/open |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 567 | 1553 | 958 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
434 | Dist - MED35 | Henderson i40607 | HENDERSON NORTH 115KV - HENDERSON N INDUSTRIAL 23KV | 9/14/2018 00:25 | 9/14/2018 09:00 | 4818263 | RECLOSER - AB FID: 8ME18_104327739 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 16 Closed Recl or Sectionalizer | NA |  |  | F2 Forced Outage | 12 Hurricane | 558 | 1375 | 515 | ENV11-ENV30 | Overhead Fac Undetermined Recloser Lockout A-B phase fault, no cause found, very windy - FLORENCE A-B phase fault, no cause found, very windy - FLORENCE | FMS 2 phase LL predicted fault between ENV11-ENV30. Line in area of trees but tech didn't find cause. A&B phase on G&W opened, tech had DCC close recloser and held. ~~~ 9/16/2018 ¦ i40607 ¦ Completion Codes or Remarks
435 | Dist - MED35 | Cary JOCHRIS | FUQUAY BELLS LAKE 230KV - PENNY ROAD 23KV | 9/14/2018 00:25 | 9/14/2018 01:26 | 4818264-2 | OCB - ABC FID: T4866B02 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1023 | 1882 | 61 |  | Missing Missing Missing | O. Christian - 10/22/2018 - CYME placed the fault location at or near 6877K and 14BR00. Patrolled on each side of each location and found nothing that would indicate having been in contact with the conductor. Nothing located on the conductors, poles, or line hardware indicating contact or cause of this outage. First responding line tech found nothing which caused outage at time of outage. DCC energized FDB and FCB held. No pictures. ~~~ 10/22/2018 (38 days) ¦ JOCHRIS ¦ Investigative Action
436 | Dist - MED35 | Zebulon omshistproc | CASTALIA 230KV - MATTHEWS CROSSROADS 24KV | 9/14/2018 00:46 | 9/14/2018 01:32 | 4818273-1 | OCB - ABC FID: T6040B12 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 944 | 950 | 46 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
437 | Dist - MED35 | Cary omshistproc | RALEIGH OAKDALE 230KV - ROYLENE 23KV | 9/14/2018 01:25 | 9/14/2018 02:23 | 4818296-2 | RECLOSER - AB FID: 1CEQ10_115158442 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 890 | 2804 | 58 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
438 | Dist - MED35 | Henderson i40607 | WARRENTON 115KV - WARRENTON INDUSTRIAL 23KV | 9/14/2018 04:13 | 9/14/2018 10:26 | 4819378 | RECLOSER - ABC FID: EA265_112850461 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | 22 Inadequate Clearances | 16 Closed Recl or Sectionalizer | NA |  |  | F2 Forced Outage | 12 Hurricane | 826 | 1247 | 373 | ECF04 | Overhead Fac Overhead Primary Failure (No Tree Involved) Slack Conductor/Sag/Improper Roll PHASES GOT TOGETHER. | G&W Recloser EA265 locked out because conductor laid out for reconductoring and phase were slapping together due to wind between ECF04-ECF32 ~~~ 9/16/2018 ¦ i40607 ¦ Completion Codes or Remarks
439 | Dist - MED35 | Sanford omshistproc | JONESBORO 230KV - OLIVIA 24KV | 9/14/2018 05:53 | 9/14/2018 10:36 | 4820218 | OCB - ABC FID: T2141B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 42 Replaced Crossarm/Brace | C2 Crossarm, Penta |  |  | F2 Forced Outage | 03 Wind | 831 | 846 | 284 | Node~1734762 | Overhead Fac Crossarm Failure Broke | ... NO OUTAGE REVIEW INFO
440 | Dist - MED35 | Garner c72037 | FUQUAY 230KV - FUQUAY 23KV | 9/14/2018 06:38 | 9/14/2018 17:22 | 4829235 | RECLOSER - ABC FID: 17ET32_104160155 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1948 | 2336 | 644 |  | Missing Missing Missing | MHS- Ran FMS and CYME rode out locations and found nothing. no pics or outage review ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Investigative Action
441 | Dist - MED35 | Raleigh omshistproc | RALEIGH YONKERS ROAD 115KV - CRABTREE CREEK 24KV | 9/14/2018 07:01 | 9/14/2018 09:16 | 4821002 | RECLOSER - B FID: 0C08BK_104336296 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 640 | 2151 | 135 |  | Missing Missing Missing FAULT APPEARS TO BE BETWEEN RDS00-RDR3 OR BETWEEN RDR44-RDQ32 | ... NO OUTAGE REVIEW INFO
442 | Dist - MED35 | Cary JOCHRIS | NEW HILL 230KV - NEW HILL 23KV | 9/14/2018 08:23 | 9/14/2018 22:28 | 4834894 | OCB - ABC FID: T5911B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HF R Dig-in(Duke) correct depth | 37 Removed Limb or Tree From Lin | 29 Conductor, bare | OR Oak, red | 21 | F2 Forced Outage | 04 Wind, Rain and Lightning | 1111 | 1226 | 845 |  | Missing Missing Missing | O. Christian - 10/10/2018 - 10" live red oak tree infested with vines 21' off CL broke off 27' above the ground contacting line and taking out FCB and 1111 customers. Tree removed from line and service restored. No damage to poles, conductors or pole line hardware. ~~~ 10/10/2018 (26 days) ¦ JOCHRIS ¦ Investigative Action
443 | Dist - MED35 | Garner c72037 | CLAYTON 115KV - AMELIA CHURCH 24KV | 9/14/2018 09:21 | 9/14/2018 11:08 | 4822725 | RECLOSER - BC FID: JM62BJ_104754852 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1269 | 2743 | 107 |  | Missing Missing Missing | MHS- no information for this outage. Ran FMS and CYME found nothing at locations. no pic or outage review ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Completion Codes or Remarks
444 | Dist - MED35 | Garner c72037 | ANGIER 230KV - CHALYBEATE 23KV | 9/14/2018 10:04 | 9/14/2018 16:23 | 4824205-2 | RECLOSER - ABC FID: P364BH_2674731 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 1529 | 1930 | 379 |  | Missing Missing Missing | MHS- ran FMS and CYME could not get a location no pics or outage review ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Completion Codes or Remarks
445 | Dist - MED35 | Garner omshistproc | ANGIER 230KV - CHALYBEATE 23KV | 9/14/2018 10:04 | 9/14/2018 12:23 | 4824205-1 | OCB - ABC FID: T5427B03 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 742 | 1930 | 139 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
446 | Dist - MED35 | Chatham County AArias | SILER CITY 115KV - ROCKY RIVER 24KV | 9/14/2018 10:05 | 9/14/2018 15:19 | 4826223 | RECLOSER - ABC FID: 6HV05_104617066 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 27 Other/See Notes | NA | NA R |  | F2 Forced Outage | 17 Wind and Rain | 1162 | 1689 | 314 | Node~103279972 | Missing Missing Missing | aarias// no outage info. Outage times could be determined from FMS ~~~ 9/26/2018 ¦ AArias ¦ Completion Codes or Remarks
447 | Dist - MED35 | Selma omshistproc | SELMA 230KV - MICRO 23KV | 9/14/2018 10:13 | 9/14/2018 19:18 | 4833561 | OCB - ABC FID: T5970B08 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1913 | 2064 | 545 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
448 | Dist - MED35 | Asheboro omshistproc | ROBBINS 115KV - ROBBINS CITY 23KV | 9/14/2018 10:25 | 9/14/2018 12:54 | 4823295 | RECLOSER - A C FID: 2089_2388107 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 39 Repaired Overhead Conductor | 29 Conductor, bare |  |  | F2 Forced Outage | 03 Wind | 646 | 1533 | 149 | Recloser~2089_2388107 | Overhead Fac Overhead Primary Failure (No Tree Involved) Conductor Broke/Burned Down 1/0 copper burnt down 1/0 copper burnt down | ... NO OUTAGE REVIEW INFO
449 | Dist - MED35 | Durham AArias | HOPE VALLEY - 14061204 | 9/14/2018 10:26 | 9/14/2018 11:58 | 10902132 | S-RCL - ABC Size: 800 VPST FID: 398753914 | 02 Line Recloser | OH Distribution Line Overhead | EA Weather | 21 Slack Conductors | M3 Copper | NA | NA R |  | F2 Forced Outage | 12 Hurricane | 1194 | 1524 | 92 | aarias// Francis St, 1 span East of Legion Ave | CMPL 2018-09-14 12:04:00 by BGFILER RMK: CMPL 2018-09-14 11:56:00 by NZJACKS RMK: RECLOSER LOCKOUT. TARGETS A-B-C. FMAG 3018. POSSIBLE FAULT LOCATION IS FRANCIS & LEGION AVE | aarias// hurricane in area. Slack field phase wire made contact with remaining phases due to high winds, created a midspan fault. No evidence of vegetation related damage. Recommend repulling field phase ~~~ 9/15/2018 ¦ AArias ¦ Work Order(s) Generated
450 | Dist - MED35 | Garner c72037 | FUQUAY 230KV - FUQUAY 23KV | 9/14/2018 10:50 | 9/15/2018 13:27 | 4831570 | OCB - A FID: T4710B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 12 Hurricane | 1131 | 2336 | 1597 |  | Missing Missing Missing | MHS-no DIS# ran FMS AND CYME rode line out and found nothing. no pics or outage review ~~~ 10/18/2018 (33 days) ¦ c72037 ¦ Completion Codes or Remarks
451 | Dist - MED35 | Garner c72037 | FUQUAY 230KV - FUQUAY SOUTH PARK 23KV | 9/14/2018 11:01 | 9/14/2018 11:57 | 4823985-2 | OCB - ABC FID: T4710B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 2966 | 3385 | 56 |  | Missing Missing Missing | MHS-no DIS# ran FMS AND CYME rode line out and found nothing. no pics or outage review ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Completion Codes or Remarks
452 | Dist - MED35 | Zebulon omshistproc | KNIGHTDALE SQUARE D 230KV - EAGLE ROCK 24KV | 9/14/2018 11:21 | 9/14/2018 17:23 | 4828342 | RECLOSER - ABC FID: 13QM87_104280994 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 534 | 622 | 362 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
453 | Dist - MED35 | Cary JOCHRIS | CARY TRIANGLE FOREST 230KV - CHURCHILL 23KV | 9/14/2018 12:00 | 9/14/2018 15:01 | 4824465 | OCB - ABC FID: T4605B03 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 2350 | 1627 | 181 |  | Missing Missing Missing | O. Christian - 10/22/2018 - CYME placed fault location near F495K. Patrolled 2-3 spans each side of F495K and found nothing that looked as though it had contacted line causing outage. Talked to responding line tech and nothing was found on line at time of outage. DCC instructed to close FCB, did so and breaker held. No pictures. ~~~ 10/22/2018 (38 days) ¦ JOCHRIS ¦ Investigative Action
454 | Dist - MED35 | Raleigh e68825 | LEESVILLE WOOD VALLEY 230KV - MACON ROAD 24KV | 9/14/2018 12:08 | 9/14/2018 17:10 | 4829066-1 | RECLOSER - ABC FID: GA15BL_104179790 | 08 Disconnect | OH Distribution Line Overhead | 03 Vegetation | HT Unfused span(s) | DV Visible stem decay | 29 Conductor, bare | HK Hickory | 30 | F2 Forced Outage | 12 Hurricane | 538 Cust Eq: 1107 | 1775 | 302 | KW60BL-7TC15 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None Large tree fell on primary & neutral causing lines down across Norwood Rd. OH primary and nuetral are down from KW60BL to 7TC | Fontana 9/27/18 & PEEL 11/16/18: - 3' dia. x 60' tall Hickory 30 feet from the feeder CL, rotten at the base, broke at the base & fell onto & the tore down the single phase unfused tap KW60BL-7TC15 & locked out the FCB. The Self-Healing Team ÃƒÂ¢Ã‚Â€Ã‚ÂœTieÃƒÂ¢Ã‚Â€Ã‚Â recloser GA15BL closed 17:10 picking up load to the Macon Rd. fdr. recloser 17G113. 1107 customers saved. Crews opened ABS 156X20 to isolate the damaged line section, & closed the FCB at 18:19 to restore 538 custs. (Hurricane Florence) ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
455 | Dist - MED35 | Garner c72037 | FUQUAY 230KV - FUQUAY SOUTH PARK 23KV | 9/14/2018 12:24 | 9/15/2018 19:24 | 4826936 | OCB - ABC FID: T4710B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 3379 | 3385 | 1860 |  | Missing Missing Missing | MHS-Ran FMS and CYME found nothing no pics or outage review ~~~ 10/18/2018 (33 days) ¦ c72037 ¦ Completion Codes or Remarks
456 | Dist - MED35 | Garner omshistproc | AUBURN 230KV - MOUNT MORIAH 23KV | 9/14/2018 12:44 | 9/15/2018 10:03 | 4825448 | RECLOSER - ABC FID: NK71BJ_103577407 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 705 | 1052 | 1279 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
457 | Dist - MED35 | Durham omshistproc | GARRETT RD - 14202413 | 9/14/2018 12:52 | 9/14/2018 15:02 | 10902663 | FOH - BC Size: 125 SMU-20 (E) FID: 38863486 | 03 Line Fuse | OH Distribution Line Overhead | 03 Vegetation | EA Cause Not Coded in Weather | 37 Removed Limb or Tree From Lin | 29 Conductor, bare |  |  | F2 Forced Outage | 12 Hurricane | 633 | 5339 | 130 | tree laying on lines, walking trail just past chim | tree laying on lines, walking trail just past chimney ridge | ... NO OUTAGE REVIEW INFO
458 | Dist - MED35 | Garner c72037 | ANGIER 230KV - CHALYBEATE 23KV | 9/14/2018 13:02 | 9/14/2018 19:51 | 4834430-1 | RECLOSER - ABC FID: P013BH_107809790 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 12 Hurricane | 1117 | 1930 | 409 |  | Missing Missing Missing | MHS - Ran FMS and CYME found nothing at locations, no pics or outage review ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Completion Codes or Remarks
459 | Dist - MED35 | Garner omshistproc | ANGIER 230KV - CHALYBEATE 23KV | 9/14/2018 13:02 | 9/14/2018 21:16 | 4834430-2 | OCB - ABC FID: T5427B03 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 666 | 1930 | 494 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
460 | Dist - MED35 | Garner c72037 | GARNER WHITE OAK 230KV - WHITE OAK 24KV | 9/14/2018 13:23 | 9/14/2018 18:39 | 4831649 | OCB - ABC FID: T4730B13 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 12 Hurricane | 1830 | 1908 | 316 |  | Missing Missing Missing | MHS- Ran FMS and CYME rode out locations and found nothing, no pics or outage review ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Completion Codes or Remarks
461 | Dist - MED35 | Garner omshistproc | DUNCAN 230KV - DUNCAN 24KV | 9/14/2018 13:53 | 9/14/2018 18:39 | 4826169-1 | RECLOSER - AB FID: J805BH_103783585 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 525 | 2587 | 287 | Node~25738320 | Missing Missing Missing wire down 1 span #2 K621BH | ... NO OUTAGE REVIEW INFO
462 | Dist - MED35 | Asheboro omshistproc | ASHEBORO EAST 115KV - ASHEBORO EAST HIGHWAY 64 23KV | 9/14/2018 14:25 | 9/14/2018 15:03 | 4826685 | RECLOSER - ABC FID: L129AD_103522824 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 681 | 1749 | 38 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
463 | Dist - MED35 | Sanford omshistproc | SANFORD GARDEN STREET - SOUTH HORNER 23KV | 9/14/2018 14:35 | 9/14/2018 15:57 | 4826790-2 | RECLOSER - ABC FID: 100F72_115177021 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 608 | 1585 | 81 | Line~0530AC_0535AC_2439664 | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
464 | Dist - MED35 | Garner c72037 | MILBURNIE 230KV - BELTLINE 23KV | 9/14/2018 15:57 | 9/14/2018 16:16 | 4828122 | RECLOSER - ABC FID: GT69BJ_104342196 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 12 Hurricane | 3981 | 1100 | 19 |  | Missing Missing Missing | MHS- Ran FMS and CYME found nothing at the locations ~~~ 10/18/2018 (34 days) ¦ c72037 ¦ Completion Codes or Remarks
465 | Dist - MED35 | Raleigh e68825 | LEESVILLE WOOD VALLEY 230KV - MACON ROAD 24KV | 9/14/2018 17:08 | 9/14/2018 18:19 | 4829066-2 | OCB - ABC FID: T5165B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | HT Unfused span(s) | DV Visible stem decay | 29 Conductor, bare | HK Hickory | 30 | F2 Forced Outage | 12 Hurricane | 1,770 Cust Eq: 1107 | 1775 | 71 | KW60BL - 7TC15 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None Large tree fell on primary & neutral causing lines down across Norwood Rd. OH primary and nuetral are down from KW60BL to 7TC | Fontana 9/27/18 & PEEL 11/16/18: - 3' dia. x 60' tall Hickory 30 feet from the feeder CL, rotten at the base, broke at the base & fell onto & the tore down the single phase unfused tap KW60BL-7TC15 & locked out the FCB. The Self-Healing Team Ã¢Â€ÂœTieÃ¢Â€Â recloser GA15BL closed 17:10 picking up load to the Macon Rd. fdr. recloser 17G113. 1107 customers saved. Crews opened ABS 156X20 to isolate the damaged line section, & closed the FCB at 18:19 to restore 538 custs. (Hurricane Florence) ~~~ 9/27/2018 ¦ e68825 ¦ Investigative Action
466 | Dist - MED35 | Sanford omshistproc | SANFORD HORNER BLVD. 230KV - COLONIAL ACRES 23KV | 9/14/2018 17:15 | 9/14/2018 22:49 | 4835108 | RECLOSER - ABC FID: S783AC_2495045 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 569 | 2085 | 334 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
467 | Dist - MED35 | Garner omshistproc | FUQUAY 230KV - FUQUAY 23KV | 9/14/2018 17:22 | 9/15/2018 13:28 | 4831648 | OCB - C FID: T4710B01 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1269 | 2336 | 1205 |  | Missing Missing Missing BROOKSIDE SUB STILL OUT 9/15 | ... NO OUTAGE REVIEW INFO
468 | Dist - MED35 | Raleigh omshistproc | RALEIGH HOMESTEAD 230KV - PERRY CREEK 23KV | 9/14/2018 17:22 | 9/14/2018 18:19 | 4829305 | RECLOSER - ABC FID: 18LN79_105985246 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 590 | 2164 | 57 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
469 | Dist - MED35 | Cary omshistproc | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 9/14/2018 17:30 | 9/14/2018 21:55 | 4831916 | RECLOSER - C FID: 5DF10_112849190 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 774 | 2825 | 265 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
470 | Dist - MED35 | Garner omshistproc | DUNCAN 230KV - DUNCAN 24KV | 9/14/2018 18:40 | 9/14/2018 18:49 | 4833467 | RECLOSER - AB FID: J805BH_103783585 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 525 | 2587 | 9 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
471 | Dist - MED35 | Garner omshistproc | DUNCAN 230KV - DUNCAN 24KV | 9/14/2018 18:52 | 9/15/2018 12:37 | 4834277 | RECLOSER - AB FID: 1CJP10_113930618 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 501 | 2587 | 1064 |  | Missing Missing Missing line cut at 7rq90 towards 7rq91 (2) spans primary and neutral down at 7rq93/ | ... NO OUTAGE REVIEW INFO
472 | Dist - MED35 | Durham rlw2159 | STALLINGS RD RET - 14281202 | 9/14/2018 18:53 | 9/14/2018 20:11 | 10904206 | S-CKT - ABC Size: Class 3 FID: 53958855 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA |  |  | F2 Forced Outage | 12 Hurricane | 843 | 847 | 78 | no idea | CMPL 2018-09-14 20:23:00 by BNADCOC RMK: nno cause found, ADCOCK, GOOCH | RLW2159-med day hurricane Florence... spoke to crew-circuit was ridden and no problem found. ~~~ 9/15/2018 ¦ rlw2159 ¦ Completion Codes or Remarks
473 | Dist - MED35 | Sanford omshistproc | SANFORD GARDEN STREET - SANFORD GARDEN STREET HOSPITAL 23KV | 9/14/2018 19:23 | 9/15/2018 21:21 | 4837206 | RECLOSER - A C FID: 0021AC_2485393 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 578 | 1762 | 1559 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
474 | Dist - MED | Garner omshistproc | HOLLY SPRINGS 230KV - BRACKENRIDGE 24KV | 9/15/2018 17:02 | 9/15/2018 20:34 | 4841986 | RECLOSER - ABC FID: 17KQ26_104223094 | 02 Line Recloser | OH Distribution Line Overhead | 05 Planned (IEEE) | HZ Cause undetermined | 27 Other/See Notes |  |  |  | P2 Scheduled Outage | 03 Wind | 816 | 1824 | 212 |  | Planned Outage OH - Repair/Replace Existing Facilities Other - OH | ... NO OUTAGE REVIEW INFO
475 | Dist - MED | Chapel Hill omshistproc | WHITE CROSS - 19051203 | 9/15/2018 19:50 | 9/16/2018 00:34 | 10908925 | RCL - ABC Size: 200 L FID: 38999647 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | 28 Other Failure Mode | 29 Permanent Repair | 29 Conductor, bare |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 576 | 930 | 283 | West of Neville & Old Greensboro Hwy | CMPL 2018-09-16 00:37:00 by SCHAMBE RMK: 200 L RECL SHOWING OUT...tree on line OLD GREENSBORO AND NEVILLE | SPOKE WITH TREE CREW @900 SPOKE WITH FLAGGERS @905... NO OUTAGE REVIEW INFO
476 | Dist - MED | Garner c72037 | FUQUAY 230KV - FUQUAY SOUTH PARK 23KV | 9/15/2018 21:18 | 9/16/2018 12:41 | 4844383 | OCB - ABC FID: T4710B03 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 03 Vegetation | DE Prior damage | 29 Permanent Repair | 29 Conductor, bare | PT PINE | 0 | F2 Forced Outage | 12 Hurricane | 2971 | 3385 | 923 | 7EX67 | Tree/Vegetatn Tree Inside Right of Way (Fall/Lean On Primary) None 477 DOWN AT 7EX67 two fauls showing at dis # 127731 and F056BH | MHS- according to service man it was a live pine tree that fell on all 3 phases and broke wire in several spots. the tree fell down in a wet land and could not get close for pics. ~~~ 10/4/2018 (18 days) ¦ c72037 ¦ Investigative Action
477 | Dist - MED | Raleigh omshistproc | METHOD 230KV - RIDGE ROAD 12KV | 9/16/2018 00:39 | 9/16/2018 00:44 | 4842893 | OCB - ABC FID: T4990B34 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 05 Planned (IEEE) | HZ Cause undetermined | 27 Other/See Notes |  |  |  | P2 Scheduled Outage | 03 Wind | 812 | 870 | 6 |  | Planned Outage OH - Repair/Replace Existing Facilities Other - OH WIRE DOWN BF68BL | ... NO OUTAGE REVIEW INFO
478 | Dist - MED | Asheboro i25781 | RAMSEUR 115KV - FRANKLINVILLE 24KV | 9/16/2018 00:41 | 9/16/2018 06:22 | 4842898 | OCB - ABC FID: T1390B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HT Unfused span(s) | DC Internal stem decay | NA | OA Oak | 19 | F2 Forced Outage | 17 Wind and Rain | 1995 | 1996 | 341 | 3027AD | Missing Missing Missing | JWW// On 9/16/18 at 00:41 during hurricane Florence a limb fell on a single phase primary that was not fused causing the Franklinville FDR to lockout and 1995 customers to lose power. When line crew arrived they got the primary back up and installed a cutout on the take off pole (3025AD). DCC energized the FDR at 06:22. ~~~ 9/20/2018 ¦ i25781 ¦ Investigative Action
479 | Dist - MED | Cary omshistproc | NEW HILL 230KV - NEW HILL 23KV | 9/16/2018 02:27 | 9/16/2018 13:50 | 4843117 | RECLOSER - ABC FID: 627K_2585269 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 528 | 1226 | 683 | Line~587K_A279K_2551890 | Missing Missing Missing line down a2479k - 587k | ... NO OUTAGE REVIEW INFO
480 | Dist - MED | Chatham County AArias | SILER CITY 115KV - BONLEE 24KV | 9/16/2018 17:52 | 9/16/2018 18:30 | 4848047 | OCB - ABC FID: T1530B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 14 Closed Breaker | NA | NA R |  | F2 Forced Outage | 16 R Unknown | 1189 | 917 | 38 |  | Missing Missing Missing | aarias// MED - hurricane Florence. No location given, FMAG puts fault right outside substation on W Raleigh St between Ingle St and George St ~~~ 9/26/2018 ¦ AArias ¦ Investigative Action
481 | Dist - MED | Asheboro omshistproc | ASHEBORO WEST 115KV - UWHARRIE STREET 23KV | 9/16/2018 18:15 | 9/17/2018 09:55 | 4848173 | RECLOSER - ABC FID: 94G18_104799859 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 559 | 2792 | 940 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
482 | Dist - MED | Chapel Hill omshistproc | WHITE CROSS - 19051203 | 9/16/2018 18:46 | 9/16/2018 19:02 | 10915920 | S-CKT - ABC Size: Class 3 FID: 38358525 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 28 Other Cause | 28 Other Failure Mode | 32 Pole Tied Up Temporarily |  |  |  | P4 Crew Initiated Outage |  | 930 | 930 | 16 | 211 RED DRUM ROAD | OPENED BREAKER TO MAKE POLE SAFE ON E#10915500. POLE WAS ON FIRE. RANDY HOUNSHELL | ... NO OUTAGE REVIEW INFO
483 | Dist - MED | Garner c72037 | RALEIGH WORTHDALE 230KV - GLENBROOK 23KV | 9/18/2018 12:30 | 9/18/2018 13:50 | 4857250 | OCB - ABC FID: T5168B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HT Unfused span(s) | 49 Replaced Transformer | 48 Transformer | NA R | 0 | F2 Forced Outage | 00 Calm | 1607 | 1608 | 80 | FK31BJ | Missing Missing Missing | MHS- overhead transformer faulted locking out FCB. crew cleared transformer and had DCC reenergize the FCB back up. crew replaced transformer and installed cutout ~~~ 10/4/2018 (16 days) ¦ c72037 ¦ Investigative Action
484 | Dist - MED | Cary JOCHRIS | CARY EVANS ROAD 230KV - EVANS ROAD 24KV | 9/19/2018 15:55 | 9/19/2018 16:16 | 4861877-1 | OCB - ABC FID: T4602B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | 09 Accident, public | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 00 Calm | 1762 | 1775 | 21 |  | Overhead Fac Undetermined FCB Lockout Under Hot Line Tag (Comments) tree hittling line | O. Christian - 10/8/2018 - Truck turning from Chapel Hill Road onto Woodland Drive "snagged' the phone joint use attachment which was low hanging between 4521K-4520K causing pole 4521K to be pulled over approximately 15-20 degrees causing conductors to contact a tree down stream and the outage of 1762 customers. Line re-energized and service restored. Also refer to outage 4862720-1,-2. ~~~ 10/8/2018 (19 days) ¦ JOCHRIS ¦ Investigative Action
485 | Dist - MED | Sanford i25781 | SANFORD GARDEN STREET - SOUTH HORNER 23KV | 9/19/2018 16:26 | 9/19/2018 18:53 | 4862048-1 | OCB - ABC FID: T2432B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M6 CCA | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 1577 | 1585 | 147 | S387AC | Human Interf OH - Vehicle None isolted problem RONALD GREGORY NO NUMBER GIVEN | JWW// On 9/19/18 at 16:26 a truck caught the cablevision at S387AC causing the feeder to lock out and 1585 customers to loose power. When the service tech arrived he cut jumpers at S382AC and had DCC energize the feeder restoring power to 1577 customers while only leaving 8 customers to change the broke pole. No pictures. ~~~ 10/3/2018 ¦ i25781 ¦ Investigative Action
486 | Dist - MED | Cary JOCHRIS | CARY EVANS ROAD 230KV - EVANS ROAD 24KV | 9/19/2018 18:51 | 9/19/2018 19:49 | 4862720-1 | OCB - ABC FID: T4602B01 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 05 Planned (IEEE) | 30 Error, Duke Contractor | 27 Other/See Notes | P2 Pole, CCA |  |  | P2 Scheduled Outage | 00 Calm | 1762 | 1775 | 58 |  | Planned Outage OH - Repair/Replace Damaged or Failed Facilities Other - OH emer drop to make repairs - pole and overhead wire charles osteen 910-217-3393//ok per nate lewis | O. Christian - 10/8/2018 - Contractor placed HLT on line after truck "snagged" low hanging communication circuit between 4521K-4520K and pulled over pole at 4521K causing conductors to get into tree causing outage 4861877_1, _2 so that pole could be straightened up. With HLT in place contractor placed "pole grabbers" on boom onto pole in an effort to straighten pole 4521K. While attempting to straighten pole conductors swung together knocking out 1762 customers and the OCB which was under a HLT. Work continued, pole straightened FCB re-energized, service restored. ~~~ 10/8/2018 (19 days) ¦ JOCHRIS ¦ Investigative Action
487 | Dist | Garner c72037 | CLAYTON INDUSTRIAL 115KV - PONY FARM 24KV | 9/22/2018 15:55 | 9/22/2018 18:34 | 4868429-1 | SWITCH - ABC FID: KF99BJ_1675051 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA | NA R | 0 | F2 Forced Outage | 00 Calm | 685 | 1114 | 159 | 9M211 | Human Interf OH - Vehicle None CAR HIT POLE LITTLE CREEK CHURCH ROAD | MHS-Public vehicle left the road and hit our pole breaking pole about 3' from ground level. crew opened up switch at KH48BJ and closed in Switch at KF99BJ getting 685 of the customers back on. the remaining 60 stayed off till job was done. ~~~ 10/4/2018 ¦ c72037 ¦ Investigative Action
488 | Dist | Roxboro i67431 | ROXBORO SOUTH 230KV - BUSHY FORK 23KV | 9/23/2018 15:26 | 9/23/2018 16:11 | 4869110-2 | RECLOSER - ABC FID: EUR63_106043388 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole |  | P1 R Packard |  | F2 Forced Outage | 00 Calm | 2170 | 2516 | 45 | EUT18 | Human Interf OH - Vehicle None BOX TRUCK HIT POLE | DPW: This is a SHN, that is controlled by DCC, does not automatically operate. Opened load side disconnect on Regulator 14XC89. DCC tied in Roxboro City (closed in Recloser EUR63) to back feed Bushy Fork up to the fault location, picking up 2170 customers. When pole was replaced DCC put feed back to normal. ~~~ 9/26/2018 ¦ i67431 ¦ Investigative Action
489 | Dist | Durham rlw2159 | DURHAM MAIN - 14011219 | 9/24/2018 12:38 | 9/24/2018 18:44 | 10926895 | S-CKT - ABC Size: Class 3 FID: 38355549 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P1 Pole, Creosote | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 1259 | 1256 | 366 | POLE AT FID#39445330 | LOCKOUT - FAULT BG - FMAG 5044 - POSSIBLE FAULT NEAR STATION AT DACIAN AND N DUKE ST - PRIMARY DOWN AND BROKE 50/3 DOUBLE CIRCUIT POLE AT INTERSECTION OF W KNOX ST AND N DUKE ST. - SPAN OF OPEN WIRE DOWN AND 1 PRIMARY | rlw2159-pole broken by hit and run driver. Pole had to be replaced. Related to 10927139. WILL NEED TO DROP DURHAM MAIN 1216 ALSO - 1216 IS ON AUX - WILL NEED TO DROP AT APPROX 1530 / MAC CST ON CIRCUIT NOTIFIED AT 1500 - OUTAGE ON 1216 WILL LAST APPROX 1 HOUR FROM TIME OF DROP SWITCHING WAS AVAILABLE FOR DURHAM MAIN 1219 AND 1216 - FIELD DECLINED TO SWITCH ~~~ 9/26/2018 ¦ rlw2159 ¦ Investigative Action
490 | Dist | Durham rlw2159 | DURHAM MAIN - 14011216 | 9/24/2018 15:57 | 9/24/2018 18:54 | 10927139 | S-CKT - ABC Size: Class 1A FID: 38355525 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P1 Pole, Creosote | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 00 Calm | 2100 | 2212 | 177 | Pole at FID#39445330 | EMERGENCY DROP - RELATED TO EV10926895 - 1216 being carried by 12ax - opened 12ax due to broken double circuit pole - one hour as of 1600 - only MAC customer on circuit has been contacted fire department and spoke with capt hammel | rlw2159-pole broken by hit and run driver. Pole had to be replaced. Circuit had to be dropped while primary was put back up. Related to 10926893 and 10926895. WILL NEED TO DROP DURHAM MAIN 1216 ALSO - 1216 IS ON AUX - WILL NEED TO DROP AT APPROX 1530 / MAC CST ON CIRCUIT NOTIFIED AT 1500 - OUTAGE ON 1216 WILL LAST APPROX 1 HOUR FROM TIME OF DROP SWITCHING WAS AVAILABLE FOR DURHAM MAIN 1219 AND 1216 - FIELD DECLINED TO SWITCH SWITCHING WAS AVAILABLE FOR DURHAM MAIN 1219 AND 1216 - FIELD DECLINED TO SWITCH ~~~ 9/26/2018 ¦ rlw2159 ¦ Investigative Action
491 | Dist | Zebulon i70604 | ROCKY MOUNT 230KV - DOMESTIC 23KV | 9/30/2018 01:09 | 9/30/2018 09:29 | 4873352 | RECLOSER - ABC FID: C753BC_104387989 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | MN Salt | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 1166 | 1974 | 500 | Line~C929BC | Human Interf OH - Vehicle None Party hit pole C929BC breaking pole causing recloser to lock out Party hit pole C929BC breaking pole causing recloser to lock out | CPS// Public vehicle struck pole dis#C929BC causing pole to break and G&W recloser C753BC to open// Responding L&S Techs replaced pole and restored customers behind G&W C753BC // No pictures of old pole // Damage included broken pole damaged 25KVA OH transformer and insulators ~~~ 10/2/2018 ¦ i70604 ¦ Investigative Action
492 | Dist | Durham dlm4375 | DURHAM MAIN - 14011219 | 10/8/2018 15:51 | 10/8/2018 16:16 | 10939755 | S-CKT - ABC Size: Class 3 FID: 38355549 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 14 Closed Breaker | NA |  |  | F2 Forced Outage | 00 Calm | 1219 | 1256 | 25 | 80K DIP OFF OF DOMINION | LOCK OUT/CHRIS HOOFT CREWS WERE IN CLEAR AT TIME OF LOCKOUT/WILL ASSIST RIDING OUT//FMAG 1780 TRIP INST 50/ A G/HALO'D ON E CLUB BETWEEN DREXAL AND ROXOBORO. CHRIS HOOFT FOUND BLOWN 80K DIP OFF OF DOMINION ST ID:387048336. LEFT FUSE OPEN TO CLOSER BREAKER | dlm4375 we had a circuit outage see 10939755. circuit was blocked by crew. crew rode circuit found 80K blown see 10939784...crew closed circuit leaving 80k open then rode behind 80k and found nothing..Bobby Wingate rode behind 80k 10/08/18 to investigate to see why 80k blew found nothing. ... we received a call later on a cut primary cable see 10940012 at 1953... ~~~ 10/8/2018 ¦ dlm4375 ¦ Investigative Action
493 | Dist | Selma i70604 | WILSON MILLS 230KV - WEST SMITHFIELD 24KV | 10/9/2018 10:39 | 10/9/2018 10:53 | 4876961 | RECLOSER - ABC FID: 1CYP41_114625739 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | HR Reclose Block, fault occurred | M4 Composite | 47 Capacitor | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 794 | 1867 | 14 | Node~P803_104174616 | Overhead Fac Cutout/Fuse Link Failure Fuse Barrel Ruptured PER PERRY LEE FUSE BARREL RUPTURED | CPS// Fuse opened on Cap bank at dis#P803 // Hot line tag was in place during event causing Recloser at dis#1CYP41 to open // No visible damage to pole or insulators could be found so Contractor isolated the other two phases on the Cap bank and the outage was restored // Capacitor bank was slated to be removed and a new one installed as part of the WR so it was left off line // No damage to equipment ~~~ 10/10/2018 ¦ i70604 ¦ Investigative Action
494 | Dist | Durham dlm4375 | ASHE STREET - 14021203 | 10/10/2018 22:41 | 10/11/2018 01:49 | 109425351 | RCL - ABC Size: 200 L FID: 38998889 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole | P2 Pole, CCA | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 675 | 2214 | 188 |  | broke 60ft pole need 5 start class/ switching and back feed | dlm4375 med day hurricane Michael.....recloser out due to a broke 60' pole and lines down across both side of Hwy. 2101 Holloway due to vehicle accident. recloser facid 38998764...Ashe st 1203 circuit blinked see 10942533 also ~~~ 10/19/2018 ¦ dlm4375 ¦ Investigative Action
495 | Dist - MED35 | Cary | GREEN LEVEL 115KV - GREEN LEVEL 24KV | 10/11/2018 14:06 | 10/12/2018 10:34 | 4883788-2 | RECLOSER - ABC FID: 647K_107923037 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 508 | 3251 | 1229 |  | Missing Missing Missing Assigned to Sparks II | ... NO OUTAGE REVIEW INFO
496 | Dist - MED35 | Cary | GREEN LEVEL 115KV - GREEN LEVEL 24KV | 10/11/2018 14:06 | 10/12/2018 10:25 | 4883788-1 | SWITCH - ABC FID: 5523K_104248313 | 08 Disconnect |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 890 | 3251 | 1220 |  | Missing Missing Missing Assigned to Sparks II | ... NO OUTAGE REVIEW INFO
497 | Dist - MED35 | Henderson | HENDERSON 230KV - HENDERSON WEST 24KV | 10/11/2018 14:25 | 10/11/2018 22:52 | 4884088 | OCB - ABC FID: T4790B16 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1336 | 1336 | 508 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
498 | Dist - MED35 | Asheboro | ASHEBORO WEST 115KV - UWHARRIE STREET 23KV | 10/11/2018 15:05 | 10/12/2018 21:29 | 4881338 | RECLOSER - ABC FID: 1ENM49_115170464 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 760 | 2792 | 1824 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
499 | Dist - MED35 | Cary | GREEN LEVEL 115KV - WILSONVILLE 24KV | 10/11/2018 15:34 | 10/11/2018 21:34 | 4884966 | OCB - ABC FID: T4603B12 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1213 | 1403 | 361 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
500 | Dist - MED35 | Asheboro | ASHEBORO EAST 115KV - COX STREET 23KV | 10/11/2018 15:34 | 10/11/2018 16:32 | 4881536 | OCB - ABC FID: T0960B13 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 734 | 731 | 58 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
501 | Dist - MED35 | Asheboro omshistproc | ASHEBORO SOUTH 115KV - ASHEBORO SOUTH 23KV | 10/11/2018 15:42 | 10/11/2018 18:00 | 4885263 | OCB - ABC FID: T0950B03 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 651 | 1830 | 139 | Node~T0950B03_1 | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
502 | Dist - MED35 | Henderson | HENDERSON 230KV - HENDERSON MILL 24KV | 10/11/2018 16:06 | 10/12/2018 09:21 | 4886748 | OCB - ABC FID: T4790B17 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 887 | 878 | 1034 |  | Missing Missing Missing 407 E MONTGOMERY ST LARGE TREE ON LINE | ... NO OUTAGE REVIEW INFO
503 | Dist - MED35 | Roxboro | YANCEYVILLE 230KV - MILTON 12KV | 10/11/2018 16:10 | 10/12/2018 16:11 | 4892879-2 | RECLOSER - ABC FID: E3L19_104155420 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1119 | 1315 | 1441 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
504 | Dist - MED35 | Henderson | HENDERSON 230KV - CLARK STREET 24KV | 10/11/2018 16:13 | 10/11/2018 21:13 | 4884578-1 | RECLOSER - ABC FID: ELJ03_104503860 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1364 | 2005 | 300 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
505 | Dist - MED35 | Chatham County | SILER CITY 115KV - BONLEE 24KV | 10/11/2018 16:16 | 10/12/2018 15:25 | 4882218 | RECLOSER - ABC FID: 5942AF_103436145 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 576 | 917 | 1389 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
506 | Dist - MED35 | Roxboro | PERSON 500KV - HYCO LAKE 24KV | 10/11/2018 16:17 | 10/12/2018 18:39 | 4882997 | RECLOSER - ABC FID: EZA04_103069661 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 39 Repaired Overhead Conductor | 29 Conductor, bare |  |  | F2 Forced Outage | 03 Wind | 550 | 1016 | 1581 |  | Overhead Fac Overhead Primary Failure (No Tree Involved) Conductor Broke/Burned Down tree wire down ez391 LINE DOWN AT EZ391 | ... NO OUTAGE REVIEW INFO
507 | Dist - MED35 | Garner c72037 | CLAYTON 115KV - BARBER MILL 24KV | 10/11/2018 16:21 | 10/11/2018 22:44 | 4890006-1 | RECLOSER - ABC FID: 5BF84_106096477 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 12 Hurricane | 3005 | 2523 | 383 |  | Missing Missing Missing | MHS- look at location from CYME yard was already cleaned up, no pics or outage review ~~~ 10/24/2018 ¦ c72037 ¦ Completion Codes or Remarks
508 | Dist - MED35 | Chatham County | SILER CITY 115KV - SNOW CAMP ROAD 24KV | 10/11/2018 16:24 | 10/14/2018 08:49 | 4886181 | RECLOSER - ABC FID: 0523AF_2361163 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1061 | 1395 | 3865 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
509 | Dist - MED35 | Roxboro | ROXBORO 115KV - ROXBORO MILL 24KV | 10/11/2018 16:38 | 10/12/2018 16:41 | 4882742 | RECLOSER - BC FID: 17NB44_104320997 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 676 | 1910 | 1443 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
510 | Dist - MED35 | Roxboro | ROXBORO 115KV - ROXBORO CITY 24KV | 10/11/2018 16:40 | 10/11/2018 21:02 | 4885910 | OCB - ABC FID: T5240B11 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1564 | 1778 | 262 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
511 | Dist - MED35 | Chatham County | BYNUM 230KV - BYNUM 23KV | 10/11/2018 16:45 | 10/13/2018 17:00 | 4882805 | RECLOSER - A FID: N940AF_2490926 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 759 | 4107 | 2895 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
512 | Dist - MED35 | Chatham County | BYNUM 230KV - BYNUM 23KV | 10/11/2018 16:45 | 10/13/2018 17:00 | 4882833 | RECLOSER - BC FID: N940AF_2490926 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 884 | 4107 | 2895 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
513 | Dist - MED35 | Chatham County | BYNUM 230KV - FEARRINGTON 24KV | 10/11/2018 16:52 | 10/11/2018 20:35 | 4882988 | OCB - ABC FID: T1025B12 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1893 | 1897 | 223 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
514 | Dist - MED35 | Chatham County | BYNUM 230KV - JACK BENNETT 23KV | 10/11/2018 16:55 | 10/13/2018 12:43 | 4883111 | RECLOSER - ABC FID: 1D3N05_115038488 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 779 | 1899 | 2627 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
515 | Dist - MED35 | Roxboro | ROXBORO 115KV - ROXBORO MILL 24KV | 10/11/2018 17:03 | 10/12/2018 20:34 | 4893618 | SWITCH - ABC FID: E1S85_104726758 | 08 Disconnect |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 639 | 1910 | 1651 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
516 | Dist - MED35 | Roxboro | ROXBORO 115KV - ROXBORO MILL 24KV | 10/11/2018 17:08 | 10/12/2018 15:13 | 4883447 | OCB - ABC FID: T5240B13 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1905 | 1910 | 1325 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
517 | Dist - MED35 | Durham AArias | POPE ROAD - 14082403 | 10/11/2018 17:10 | 10/12/2018 08:59 | 10962259 | S-RCL - ABC Size: 800 VPTT FID: 404709669 | 02 Line Recloser | OH Distribution Line Overhead | 03 Vegetation | HZ Cause undetermined | 16 Closed Recl or Sectionalizer | NA | NA R |  | F2 Forced Outage | 12 Hurricane | 2625 | 3214 | 949 |  | RCL OPENED TO SECTIONALIZE. TRIED BRKR BLOCKED BUT LOCKED OUT. GOT B-C TARGETS UNDER RCL AND NO FMAG. J388 CHRIS BRIGGS RODE CIRCUIT TO RCL AND DID NOT FIND FAULT. - CLOSED RECLOSER UP TO RECLOSER 38998771 | aarias// MED- hurricane. Crews rode ckt, no issue found. Closed RCL and it held. Crews delayed due to extended damage across territory. Ckt last trimmed in 2010, scheduled to be trimmed in 2019. ~~~ 10/24/2018 ¦ AArias ¦ Completion Codes or Remarks
518 | Dist - MED35 | Roxboro | ROXBORO SOUTH 230KV - ROXBORO SOUTH CROWN 23KV | 10/11/2018 17:16 | 10/11/2018 19:56 | 4883451 | OCB - ABC FID: T5230B01 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1007 | 1012 | 160 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
519 | Dist - MED35 | Cary c72037 | FUQUAY BELLS LAKE 230KV - HILLTOP 23KV | 10/11/2018 17:20 | 10/11/2018 20:26 | 4883505-2 | OCB - ABC FID: T4866B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA | NA R | 0 | F2 Forced Outage | 12 Hurricane | 2,324 Cust Eq: 988 | 2345 | 186 | undetermined | Missing Missing Missing | MHS- crew rode line out and found nothing on line crew had DCC re-energize FCB ~~~ 10/18/2018 ¦ c72037 ¦ Investigative Action
520 | Dist - MED35 | Roxboro | BAHAMA 230KV - ROUGEMONT 23KV | 10/11/2018 17:23 | 10/12/2018 10:07 | 4892312 | RECLOSER - ABC FID: E1217_2580721 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1044 | 1906 | 1004 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
521 | Dist - MED35 | Cary | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 10/11/2018 17:25 | 10/11/2018 17:53 | 4884061 | OCB - ABC FID: T4866B05 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 2816 | 2825 | 29 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
522 | Dist - MED35 | Roxboro | BAHAMA 230KV - ROUGEMONT 23KV | 10/11/2018 17:25 | 10/12/2018 10:04 | 4892300 | SWITCH - ABC FID: E0384_104855244 | 08 Disconnect |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1300 | 1906 | 999 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
523 | Dist - MED35 | Henderson | OXFORD NORTH 230KV - BEREA 23KV | 10/11/2018 17:33 | 10/11/2018 20:57 | 4883695-1 | OCB - ABC FID: T5090B04 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 614 | 1947 | 204 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
524 | Dist - MED35 | Henderson | OXFORD NORTH 230KV - BEREA 23KV | 10/11/2018 17:35 | 10/11/2018 23:50 | 4888921-1 | SWITCH - ABC FID: ETF35_2873707 | 08 Disconnect |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 923 | 1947 | 376 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
525 | Dist - MED35 | Henderson | OXFORD SOUTH 230KV - STEM 23KV | 10/11/2018 17:37 | 10/12/2018 12:26 | 4883734 | OCB - ABC FID: T5085B02 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 2536 | 2535 | 1129 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
526 | Dist - MED35 | Garner | WAKE TECH 230KV - TWIN CREEKS 24KV | 10/11/2018 17:40 | 10/11/2018 20:06 | 4883774-1 | RECLOSER - ABC FID: D860BH_103378776 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 878 | 2340 | 147 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
527 | Dist - MED35 | Garner | WAKE TECH 230KV - TWIN CREEKS 24KV | 10/11/2018 17:40 | 10/11/2018 20:57 | 4883774-2 | RECLOSER - ABC FID: C217BH_108924977 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1126 | 2340 | 198 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
528 | Dist - MED35 | Henderson | OXFORD SOUTH 230KV - STEM 23KV | 10/11/2018 17:42 | 10/12/2018 13:29 | 4893053 | RECLOSER - ABC FID: 8P996_103357933 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1659 | 2535 | 1187 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
529 | Dist - MED35 | Garner | GARNER WHITE OAK 230KV - CORNWALLIS 24KV | 10/11/2018 17:42 | 10/11/2018 20:30 | 4883804 | RECLOSER - B FID: 5NG99_104520915 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 550 | 1923 | 168 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
530 | Dist - MED35 | Henderson | OXFORD NORTH 230KV - ORPHANAGE 23KV | 10/11/2018 17:45 | 10/11/2018 19:01 | 4886119 | OCB - ABC FID: T5090B03 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 935 | 1584 | 76 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
531 | Dist - MED35 | Henderson | HENDERSON 230KV - CYPRESS DRIVE 24KV | 10/11/2018 17:47 | 10/11/2018 23:08 | 4889784 | SWITCH - BC FID: ERY53_1648288 | 08 Disconnect |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1149 | 1173 | 321 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
532 | Dist - MED35 | Henderson | HENDERSON NORTH 115KV - FARM STREET 23KV | 10/11/2018 17:49 | 10/11/2018 18:13 | 4884550 | OCB - ABC FID: T4770B04 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1253 | 1242 | 24 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
533 | Dist - MED35 | Cary | CARY TRIANGLE FOREST 230KV - TRIANGLE FOREST 23KV | 10/11/2018 17:49 | 10/11/2018 23:56 | 4884027 | OCB - ABC FID: T4605B04 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1265 | 1283 | 367 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
534 | Dist - MED35 | Raleigh | LEESVILLE WOOD VALLEY 230KV - BAILEYWICK ROAD 24KV | 10/11/2018 17:50 | 10/12/2018 11:29 | 4884032 | RECLOSER - ABC FID: 17JW38_104381795 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 629 | 1627 | 1059 |  | Missing Missing Missing large tree near Tredwood Dr/ Mt Vernon Ch. Rd Poles broke/ lines down | ... NO OUTAGE REVIEW INFO
535 | Dist - MED35 | Raleigh | LEESVILLE WOOD VALLEY 230KV - WOOD VALLEY 24KV | 10/11/2018 17:54 | 10/12/2018 20:02 | 4884075 | RECLOSER - A C FID: LM53BL_103935523 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 510 | 1615 | 1568 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
536 | Dist - MED35 | Henderson | HENDERSON 230KV - CYPRESS DRIVE 24KV | 10/11/2018 17:55 | 10/11/2018 20:55 | 4884083-2 | OCB - ABC FID: T4790B18 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 661 | 1173 | 179 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
537 | Dist - MED35 | Raleigh omshistproc | CHESTNUT HILLS 115KV - NORTH GLEN 23KV | 10/11/2018 17:57 | 10/13/2018 14:32 | 4892774-2 | SWITCH - ABC FID: GP20BL_2867483 | 08 Disconnect | OH Distribution Line Overhead | 05 Planned (IEEE) | HZ Cause undetermined | 27 Other/See Notes |  |  |  | P2 Scheduled Outage | 04 Wind, Rain and Lightning | 776 | 2553 | 2675 | Load~863AZ | Planned Outage OH - Repair/Replace Damaged or Failed Facilities Other - OH STILL ON THE GROUND 01:24 10/13/2018 PER RON ADAMS | ... NO OUTAGE REVIEW INFO
538 | Dist - MED35 | Henderson | YOUNGSVILLE 115KV - POKOMOKE 24KV | 10/11/2018 17:59 | 10/12/2018 09:31 | 4884105 | RECLOSER - BC FID: 180C92_110597369 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 734 | 2550 | 932 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
539 | Dist - MED35 | Henderson | HENDERSON EAST 230KV - OAK 23KV | 10/11/2018 18:04 | 10/13/2018 19:06 | 4884237-2 | RECLOSER - ABC FID: 114C46_1668523 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 506 | 1239 | 2942 |  | Missing Missing Missing 627 EDWARDS RD TREE SPLIT ON LINE, 22 W CHAVIS RD, OUTAGE FOR MEDICAL CUST | ... NO OUTAGE REVIEW INFO
540 | Dist - MED35 | Raleigh | LEESVILLE WOOD VALLEY 230KV - BAILEYWICK ROAD 24KV | 10/11/2018 18:04 | 10/13/2018 18:49 | 4884188 | RECLOSER - A C FID: 79L17_112103687 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 526 | 1627 | 2925 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
541 | Dist - MED35 | Garner | RALEIGH WORTHDALE 230KV - ROSE LANE 23KV | 10/11/2018 18:05 | 10/11/2018 22:26 | 4884341 | RECLOSER - BC FID: 18AN42_104865052 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1219 | 1832 | 261 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
542 | Dist - MED35 | Zebulon | KNIGHTDALE SQUARE D 230KV - MIDWAY 24KV | 10/11/2018 18:21 | 10/12/2018 03:59 | 4884795 | OCB - ABC FID: T4852B13 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1650 | 1652 | 579 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
543 | Dist - MED35 | Raleigh e68825 | LAKESTONE 115KV - BECKANA 12KV | 10/11/2018 18:22 | 10/11/2018 23:30 | 4890131 | OCB - ABC FID: T4870B04 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HZ Cause undetermined | 28 Patrolled & No Problem Found | NA |  |  | F2 Forced Outage | 12 Hurricane | 818 | 1020 | 308 |  | Missing Missing Missing | A 2711 amp C-phase to ground fault caused the Beckana 12 kV FCB to lockout at 11:09 PM. Responding C&M & DA crews found no culprit, so had DCC remotely close the FCB to restore service to the feeder. Engineer performed an FMS-Cyme fault location study, and found several predicted possible feeder sections with the fault current level. Engineers patrolled these sections, but could find no culprit. All of the reported C&M responders were interviewed by the Sr. Engineer, and none responded with a definite culprit. Since this occurred during hurricane winds, we believe the culprit was either a tree or tree limb or other wind-borne object contacting the a C-phase conductor and grounded structure or the neutral. No damage... Inconclusive study. ~~~ 10/19/2018 ¦ e68825 ¦ Investigative Action
544 | Dist - MED35 | Zebulon | KNIGHTDALE SQUARE D 230KV - WIDEWATERS 24KV | 10/11/2018 18:22 | 10/12/2018 04:01 | 4884838 | OCB - ABC FID: T4852B12 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1130 | 1215 | 579 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
545 | Dist - MED35 | Garner omshistproc | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 10/11/2018 18:22 | 10/12/2018 09:36 | 4886418-2 | RECLOSER - ABC FID: 12PJ03_103837646 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA |  |  | F2 Forced Outage | 00 Calm | 582 | 2861 | 914 |  | Overhead Fac Undetermined Recloser Lockout Closed and holding | ... NO OUTAGE REVIEW INFO
546 | Dist - MED35 | Zebulon | KNIGHTDALE SQUARE D 230KV - WIDEWATERS 24KV | 10/11/2018 18:23 | 10/12/2018 04:40 | 4888599-1 | SWITCH - ABC FID: HB13BF_1660955 | 08 Disconnect |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 843 | 1215 | 616 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
547 | Dist - MED35 | Henderson omshistproc | YOUNGSVILLE 115KV - POKOMOKE 24KV | 10/11/2018 18:24 | 10/12/2018 22:17 | 4892469 | SWITCH - ABC FID: 11RA67_1671289 | 08 Disconnect | OH Distribution Line Overhead | 05 Planned (IEEE) | HZ Cause undetermined | 27 Other/See Notes |  |  |  | P2 Scheduled Outage | 00 Calm | 719 | 2550 | 1672 | Switch~11RA67_1671289 | Planned Outage OH - Repair/Replace Existing Facilities Other - OH broke poles--michael phelps jr--pike 434-709-1543 approx 18:00 broke poles--michael phelps jr--pike 434-709-1543 approx 18:00 | ... NO OUTAGE REVIEW INFO
548 | Dist - MED35 | Henderson omshistproc | HENDERSON 230KV - CHESTNUT 24KV | 10/11/2018 18:30 | 10/14/2018 21:28 | 4886725-1 | OCB - ABC FID: T4790B27 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | 12 Lockout Without Perm Fault | 27 Other/See Notes | NA |  |  | F2 Forced Outage | 04 Wind, Rain and Lightning | 519 | 187 | 4498 |  | Overhead Fac Undetermined Feeder Circuit Breaker Lockout HURRICANE 2-spans 477 pri down | ... NO OUTAGE REVIEW INFO
549 | Dist - MED35 | Henderson | WARRENTON 115KV - WARRENTON 23KV | 10/11/2018 18:36 | 10/12/2018 11:02 | 4885357-1 | OCB - ABC FID: T5360B02 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 536 | 709 | 986 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
550 | Dist - MED35 | Henderson | HENDERSON NORTH 115KV - FARM STREET 23KV | 10/11/2018 18:40 | 10/12/2018 12:26 | 4892550 | RECLOSER - ABC FID: 17MN92_104304451 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 944 | 1242 | 1066 |  | Missing Missing Missing 869 HICKSBORO RD CUSTOMER IS ON LIFE SUPPORT, 516 RADIO LN CUST ON MEDICAL EQUIPMENT | ... NO OUTAGE REVIEW INFO
551 | Dist - MED35 | Raleigh DFontan | RALEIGH TIMBERLAKE 115KV - INGRAM 23KV | 10/11/2018 18:43 | 10/11/2018 21:40 | 4885548 | OCB - ABC FID: T5311B06 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 11 Unknown Cause | HT Unfused span(s) | M2 ACSR | 29 Conductor, bare | UU Unknown Manufacturer |  | F2 Forced Outage | 12 Hurricane | 536 | 535 | 177 | K62BK-6PF21 | Missing Missing Missing | Peel 10/17/18: A-phase conductor of the 3-phase un-fused OH tap at K62BK going to K84BK broke in span K62BK-6PF21 near pole K82BK , and phase conductor still attached to pole K82BK fell onto the neutral conductor, causing an A phase to neutral fault, locking out the FCB. This occurred during hurricane winds. Nothing was found by the responding C&M line tech nor the engineers which might have hit and broke the conductor. The conductor was repaired (spliced), and the responding crew had DCC remotely close the FCB to restore service to the feeder. ~~~ 10/17/2018 ¦ DFontan ¦ Investigative Action
552 | Dist - MED35 | Henderson | HENDERSON NORTH 115KV - FARM STREET 23KV | 10/11/2018 19:03 | 10/12/2018 10:53 | 4886152 | OCB - ABC FID: T4770B04 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 1253 | 1242 | 951 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
553 | Dist - MED35 | Henderson | OXFORD NORTH 230KV - ORPHANAGE 23KV | 10/11/2018 19:09 | 10/12/2018 19:25 | 4886419 | OCB - ABC FID: T5090B03 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 789 | 1584 | 1456 |  | Missing Missing Missing 911 ticket 1278630 | ... NO OUTAGE REVIEW INFO
554 | Dist - MED35 | Zebulon | SPRING HOPE 115KV - SOUTHERN NASH 23KV | 10/11/2018 19:13 | 10/11/2018 21:07 | 4887336 | OCB - ABC FID: T6041B01 | 01 Feeder Breaker/Recl in Substa |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 854 | 946 | 114 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
555 | Dist - MED35 | Henderson | HENDERSON NORTH 115KV - WILLIAMSBORO 23KV | 10/11/2018 19:25 | 10/12/2018 15:14 | 4893240 | RECLOSER - A FID: 17EN01_104125427 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 504 | 2497 | 1189 |  | Missing Missing Missing THIS IS SAME AS BROKE POLE ON HWY 39/PLUM NUTTY | ... NO OUTAGE REVIEW INFO
556 | Dist - MED35 | Henderson | WARRENTON 115KV - NORLINA 23KV | 10/11/2018 20:02 | 10/12/2018 10:12 | 4888913-2 | SWITCH - ABC FID: EA588_1862127 | 08 Disconnect |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 728 | 1703 | 850 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
557 | Dist - MED35 | Garner | GARNER WHITE OAK 230KV - CORNWALLIS 24KV | 10/11/2018 20:31 | 10/12/2018 06:58 | 4888637 | LINE CUT - ABC FID: Line Cut-618318 | 09 Jumper/wire cut/open | OH Distribution Line Overhead | 28 Other Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 03 Wind | 1067 | 1923 | 627 |  | Natural Interf OH - Other (Comments) None STORM | ... NO OUTAGE REVIEW INFO
558 | Dist - MED35 | Cary | GREEN LEVEL 115KV - WILSONVILLE 24KV | 10/11/2018 21:56 | 10/11/2018 22:13 | 4889658 | RECLOSER - ABC FID: CCY03_2585265 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 741 | 1403 | 18 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
559 | Dist - MED35 | Garner | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 10/11/2018 22:45 | 10/12/2018 09:36 | 4890029 | RECLOSER - BC FID: 12PJ03_103837646 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 578 | 2861 | 651 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
560 | Dist - MED35 | Selma | FOUR OAKS 230KV - HANNAHS CREEK 24KV | 10/11/2018 23:51 | 10/12/2018 01:10 | 4890738-1 | RECLOSER - ABC FID: V901_104479318 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 920 | 1553 | 79 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
561 | Dist - MED | Selma | FOUR OAKS 230KV - HANNAHS CREEK 24KV | 10/12/2018 01:10 | 10/12/2018 01:56 | 4890878 | RECLOSER - ABC FID: V901_104479318 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 920 | 1553 | 46 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
562 | Dist - MED | Durham omshistproc | POPE ROAD - 14082404 | 10/12/2018 04:18 | 10/12/2018 04:44 | 10962965 | S-CKT - ABC Size: Class 2 FID: 38355933 | 01 Feeder Breaker/Recl in Substa |  | 28 Other Cause | 28 Other Failure Mode | 14 Closed Breaker |  |  |  | F2 Forced Outage |  | 883 | 3258 | 25 | WINDING WAY AND CHAPEL HILL RD | J388 CHRIS BRIGGS OPENED BRKR TO MAKE UP JUMPERS | ... NO OUTAGE REVIEW INFO
563 | Dist - MED | Chatham County omshistproc | PITTSBORO 230KV - BIG WOODS 23KV | 10/12/2018 09:20 | 10/13/2018 16:48 | 4892078 | SWITCH - ABC FID: 13EW07_2495783 | 08 Disconnect | OH Distribution Line Overhead | 05 Planned (IEEE) | HZ Cause undetermined | 27 Other/See Notes |  |  |  | P2 Scheduled Outage | 04 Wind, Rain and Lightning | 840 | 1427 | 1887 | Switch~13EW07_2495783 | Planned Outage OH - Repair/Replace Damaged or Failed Facilities Other - OH wire down at cs61af --terry kirkus-pike 3364671976--hurricane michael wire down at cs61af --terry kirkus-pike 3364671976--hurricane michael | ... NO OUTAGE REVIEW INFO
564 | Dist - MED | Garner omshistproc | RALEIGH WORTHDALE 230KV - LITTLE JOHN 23KV | 10/12/2018 09:37 | 10/12/2018 11:59 | 4892219 | RECLOSER - A FID: G0P96_104694169 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA |  |  | F2 Forced Outage | 00 Calm | 672 | 2861 | 142 |  | Overhead Fac Undetermined Recloser Lockout recloser closed and holding | ... NO OUTAGE REVIEW INFO
565 | Dist - MED | Cary omshistproc | NEW HILL 230KV - NEW HILL 23KV | 10/12/2018 12:32 | 10/12/2018 17:18 | 4893267-3 | RECLOSER - ABC FID: 627K_2585269 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D4 Burned/Exploded | 39 Repaired Overhead Conductor | 29 Conductor, bare |  |  | F2 Forced Outage | 00 Calm | 528 | 1226 | 286 | Source~T5911B01 | Overhead Fac Overhead Primary Failure (No Tree Involved) Conductor Broke/Burned Down Wire down at DIS#629K Wire down at DIS#629K | ... NO OUTAGE REVIEW INFO
566 | Dist - MED | Zebulon | ZEBULON 115KV - WAKEFIELD STREET 23KV | 10/12/2018 17:22 | 10/12/2018 23:07 | 4894065 | LINE CUT - ABC FID: Line Cut-619058 | 09 Jumper/wire cut/open | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair |  |  |  | F2 Forced Outage | 00 Calm | 613 | 1838 | 345 |  | Human Interf OH - Vehicle None Excavtor working near line hit and broke the pole | ... NO OUTAGE REVIEW INFO
567 | Dist - MED | Roxboro | ROXBORO 115KV - RIDGE ROAD 24KV | 10/12/2018 18:32 | 10/12/2018 19:16 | 4894216 | RECLOSER - ABC FID: EXS02_2563621 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 877 | 1985 | 44 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
568 | Dist - MED | Sanford omshistproc | SANFORD HORNER BLVD. 230KV - COLONIAL ACRES 23KV | 10/12/2018 22:10 | 10/12/2018 23:17 | 4894537 | RECLOSER - ABC FID: S783AC_2495045 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair |  |  |  | F2 Forced Outage | 00 Calm | 682 | 2085 | 67 | Recloser~S783AC_2495045 | Human Interf OH - Vehicle None Car hit recloser pole and damaged control. No customers were out. Pole was broken. | ... NO OUTAGE REVIEW INFO
569 | Dist - MED | Zebulon | ROCKY MOUNT 230KV - DOMESTIC 23KV | 10/12/2018 22:18 | 10/12/2018 23:46 | 4894569 | OCB - ABC FID: T5940B26 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | 29 Permanent Repair | 43 Recloser, Electronic |  |  | F2 Forced Outage | 00 Calm | 1811 | 1974 | 88 |  | Overhead Fac Overhead Switch / Recloser Failure Three Phase Recloser Failed EMER DROP - BAD DOWN STREAM DEVICE Primary out of sag contacted City of Rocky Mount span guy | ... NO OUTAGE REVIEW INFO
570 | Dist - MED | Chatham County | BYNUM 230KV - JACK BENNETT 23KV | 10/13/2018 14:21 | 10/14/2018 16:16 | 4895272 | LINE CUT - ABC FID: Line Cut-619683 | 09 Jumper/wire cut/open |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 744 | 1899 | 1555 |  | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
571 | Dist | Cary | RALEIGH OAKDALE 230KV - SUN GATE 23KV | 10/15/2018 12:37 | 10/15/2018 13:19 | 4896598-2 | RECLOSER - ABC FID: N767K_104346054 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair |  |  |  | F2 Forced Outage | 00 Calm | 1013 | 2863 | 41 | Switch~K160K_2646247 | Human Interf (Obsolete) Vehicle (Obsolete) None | ... NO OUTAGE REVIEW INFO
572 | Dist | Garner omshistproc | ANGIER 230KV - CHALYBEATE 23KV | 10/21/2018 03:30 | 10/21/2018 05:38 | 4899162-1 | RECLOSER - BC FID: N887BH_108855705 | 02 Line Recloser |  | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes |  |  |  | F2 Forced Outage | 16 R Unknown | 886 | 1930 | 128 | Recloser~N887BH_108855705 | Missing Missing Missing | ... NO OUTAGE REVIEW INFO
573 | Dist | Cary JOCHRIS | CARY EVANS ROAD 230KV - EVANS ROAD 24KV | 10/28/2018 18:34 | 10/28/2018 20:10 | 4902143-1 | RECLOSER - AC FID: 17LN10_104265321 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | 11 Unknown Cause | 27 Other/See Notes | NA |  |  | F2 Forced Outage | 00 Calm | 1016 | 1775 | 96 | Recloser~17LN10_104265321 | Overhead Fac Undetermined Recloser Lockout UNKNOWEN | O. Christian - 11/8/2018 - Fault location not determined and not found. The recloser 17LN10 monitors underground cable. Couple of PMH's checked nothing found. Line tech requested the recloser be closed, recloser closed and held. ~~~ 11/8/2018 ¦ JOCHRIS ¦ Investigative Action
574 | Dist | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 10/29/2018 11:13 | 10/29/2018 13:16 | 4902376-4 | SWITCH - ABC FID: NL63BJ_2885731 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole |  |  |  | F2 Forced Outage | 00 Calm | 589 | 2736 | 123 | T187BJ | Human Interf OH - Vehicle None CAR BROKE POLE# T187BJ | MHS- Car hit and broke pole at ground level DIS# T187BJ ~~~ 11/7/2018 ¦ c72037 ¦ Investigative Action
575 | Dist | Garner c72037 | GARNER 115KV - WOODLAND ROAD 24KV | 10/29/2018 11:13 | 10/29/2018 12:15 | 4902376-2 | OCB - ABC FID: T4720B02 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 47 Replaced Pole |  |  |  | F2 Forced Outage | 00 Calm | 759 | 2736 | 62 | LT187BJ | Human Interf OH - Vehicle None CAR BROKE POLE# T187BJ | MHS- Car hit and broke pole at ground level DIS# T187BJ ~~~ 11/7/2018 ¦ c72037 ¦ Investigative Action
576 | Dist | Cary JOCHRIS | MORRISVILLE 230KV - PRESTON 23KV | 10/30/2018 10:58 | 10/30/2018 15:07 | 4902766 | OCB - ABC FID: T5010B04 | 01 Feeder Breaker/Recl in Substa | UG Distribution Line Underground | 20 Equipment failure | D1 Broken/Malfunctioning | 29 Permanent Repair | SB Equip (not TX), padmounted | SD S&C Electric |  | F2 Forced Outage | 00 Calm | 2612 | 2593 | 249 | Switch~F759K_2670704 | Undergrnd Fac Underground Switch Failure PM Switch Failed switch gear failed Dis#F759k compartment 1 and 2 | O. Christian - 11/7/2018 - PMH9 F759K failed/flashed. Work order 25042550 written to replace unit with PME9. No pictures. ~~~ 11/7/2018 ¦ JOCHRIS ¦ Investigative Action
577 | Dist | Raleigh DFontan | METHOD 230KV - FAIRGROUNDS 12KV | 10/31/2018 15:22 | 10/31/2018 15:56 | 4903142 | OCB - ABC FID: T4990B38 | 01 Feeder Breaker/Recl in Substa | OH Distribution Line Overhead | 20 Equipment failure | HR Reclose Block, fault occurred | 29 Permanent Repair | 37 Arrester | C7 Cooper | 93 | F2 Forced Outage | 00 Calm | 679 | 679 | 34 | Load~CR89BL | Overhead Fac Overhead Arrester Failure Arrester Failed (Cooper 1992-'94) | PEEL 11/1/18: FCB was on HLT for work being done by a Pike Construction crew at pole CS00BL. At 15:22:04, a 3018.07 amp B-phase to ground fault occurred, locking the out the FCB. DCC contacted the Pike crew via radio, and the crew responded they had not caused the lockout, but had heard a boom coming from upstream of them on the feeder back towards the substation. Responding C&M techs patrolled the feeder from the span the Pike crew was working, and found a blown riser pole lightning arrester on the B-phase UG dip cable at pole 99Q04, 3 spans upstream of pole CS00BL. Also, the A-phase ug dip cutout was also found open (fuse blown). This engineer performed an FMS-Cyme fault location analysis, and found the fault location to be at pole CS00BL, and not at pole 99Q04. This engineer still suspects a mishap by the Pike Electric crew, but cannot prove it. However, engineer plans to have dip pole 99Q04 rebuilt to current specs. C&M responder re-fused the cutout, cleared the blown arrester from the line, then had DCC ~~~ 11/1/2018 ¦ DFontan ¦ Investigative Action
578 | Dist | Raleigh DFontan | LEESVILLE WOOD VALLEY 230KV - BAILEYWICK ROAD 24KV | 11/2/2018 21:52 | 11/2/2018 22:05 | 4904106 | LINE CUT - ABC FID: Line Cut-621018 | 02 Line Recloser | OH Distribution Line Overhead | 20 Equipment failure | D1 Broken/Malfunctioning | M3 Copper | 39 Disconnect | B2 Bridges Electric | 3 | P4 Crew Initiated Outage | 00 Calm | 1310 | 1627 | 13 | 11CT86 | Overhead Fac Overhead Switch / Recloser Failure Three Phase Recloser Failed | PEEL 11/5/18: After restoring Outage 4904047, C&M Tech noticed the road-(C) phase disconnect on #750 dip pole 11CT86 was arcing; apparently its blade had somehow become un-seated (perhaps due to the fault current passing through it 4 times during the recloser operations of outage 4904047). To prevent further catastrophic damage to the disconnect, the C&M Tech had DCC remotely open Recloser 79L17 to de-energize the disconnect. He then exercised the disconnect, then slammed it home to re-seat it, after which he had DCC reclose the recloser to restore service to the feeder. Engineer plans to have the disconnects replaced on this pole. ~~~ 11/5/2018 ¦ DFontan ¦ Investigative Action
579 | Dist | Zebulon i70604 | SAMARIA 115KV - FRAZIER ROAD 24KV | 11/4/2018 07:43 | 11/4/2018 12:25 | 4904559-2 | SWITCH - ABC FID: AL22BF_111540093 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | M8 Creosote | P1 Pole, Creosote | UU Unknown Manufacturer |  | P4 Crew Initiated Outage | 00 Calm | 530 | 1801 | 282 | AD79BF | Human Interf OH - Vehicle None CAR HIT POLE AT DIS#AD79BF | CPS// Public vehicle hit pole at dis#AD79BF causing it to break // Responding service tech opened hydraulic reclosers at dis#AT38BF to isolate the broken pole (step 1) // Service tech then opened non-load break disconnects at AL22BF to further minimize the customer count then closed AT38BF (step 2)// Pole was replaced and all customers were restored // Damage included broke pole, transformer, and insulators. ~~~ 11/6/2018 ¦ i70604 ¦ Investigative Action
580 | Dist | Garner c72037 | DUNCAN 230KV - WILBON 24KV | 11/4/2018 08:29 | 11/4/2018 09:35 | 4904573-1 | RECLOSER - ABC FID: 57C00_104758356 | 02 Line Recloser | OH Distribution Line Overhead | 04 Wildlife | 04 Wildlife | 29 Permanent Repair |  |  |  | F2 Forced Outage | 00 Calm | 2735 | 3375 | 66 | ADE90 | Natural Interf OH - Animal/Bird (Comments) None SQURRILL | MHS-a squrrill got across underground dip and lock out the feeder ~~~ 11/9/2018 ¦ c72037 ¦ Investigative Action
581 | Dist | Garner omshistproc | DUNCAN 230KV - WILBON 24KV | 11/4/2018 08:29 | 11/4/2018 10:34 | 4904573-2 | RECLOSER - ABC FID: K221BH_104539557 | 02 Line Recloser | OH Distribution Line Overhead | 04 Wildlife | 04 Wildlife | 29 Permanent Repair |  |  |  | F2 Forced Outage | 00 Calm | 636 | 3375 | 125 | Load~ADE90 | Natural Interf OH - Animal/Bird (Comments) None SQURRILL | ... NO OUTAGE REVIEW INFO
582 | Dist | Cary omshistproc | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 11/5/2018 13:40 | 11/5/2018 16:25 | 4904976-2 | SWITCH - ABC FID: T4630_24GX12 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair |  |  |  | F2 Forced Outage | 00 Calm | 682 | 2825 | 164 | Fuse~BY18AH_2517443 | Human Interf OH - Vehicle None TRUCK HIT POLE | ... NO OUTAGE REVIEW INFO
583 | Dist | Cary omshistproc | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 11/5/2018 13:40 | 11/5/2018 15:51 | 4904976-1 | RECLOSER - AB FID: A194_104369660 | 02 Line Recloser | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair |  |  |  | F2 Forced Outage | 00 Calm | 2562 | 2825 | 130 | Fuse~BY18AH_2517443 | Human Interf OH - Vehicle None TRUCK HIT POLE | ... NO OUTAGE REVIEW INFO
584 | Dist | Cary omshistproc | FUQUAY BELLS LAKE 230KV - NEEDMORE 23KV | 11/5/2018 13:41 | 11/5/2018 16:25 | 4904984-2 | SWITCH - ABC FID: T4630_24GX12 | 08 Disconnect | OH Distribution Line Overhead | 09 Public Accident/Damage | 16 Accident, public vehicle | 29 Permanent Repair |  |  |  | F2 Forced Outage | 00 Calm | 587 | 2825 | 164 | Fuse~BY18AH_2517443 | Human Interf OH - Vehicle None TRUCK HIT POLE | ... NO OUTAGE REVIEW INFO
585 | Dist | Raleigh DFontan | CHESTNUT HILLS 115KV - COUNTRY CLUB 23KV | 11/8/2018 08:48 | 11/8/2018 19:43 | 4905929 | LINE CUT - ABC FID: Line Cut-621438 | 03 Line Fuse | UG Distribution Line Underground | 09 Public Accident/Damage | HD Accident, public dig-in | 29 Permanent Repair | UG Cable, UG, 25KV 1/0 | UU Unknown Manufacturer |  | F2 Forced Outage | 00 Calm | 561 | 2061 | 655 | DD90BK-DE37BK | Human Interf Dig-Ins Primary Cable hti cable CUT CABLE, | PEEL 11/12/18 - A boring crew for a comms company cut into two phases of UG primary in span DD90BK - DE65BK, DE37BK, & DE66BK. DCC originally dispatched a serviceman, however, after a few hours he was still unable to locate the issue and UG cable repairman was called. He spliced the two phases of damaged primary and had the serviceman close the fuses at DD90BK to restore service to the subdivision. ~~~ 11/9/2018 ¦ DFontan ¦ Investigative Action
586 | Dist | Selma i70604 | WILSON MILLS 230KV - WEST SMITHFIELD 24KV | 11/8/2018 15:45 | 11/8/2018 16:34 | 4906101 | RECLOSER - ABC FID: 1CYP41_114625739 | 02 Line Recloser | OH Distribution Line Overhead | 11 Unknown Cause | HR Reclose Block, fault occurred | 28 Patrolled & No Problem Found | NA |  |  | F2 Forced Outage | 02 Rain | 803 | 1867 | 49 |  | Missing Missing Missing | CPS// Contract crew had G&W recloser 1CYP41 under hot line tag and they were in the process of pulling in wire when a fault occurred // The recloser opened and the cause could not be found // FMS and CYME were used to determine a location of the B to Ground fault but no visible issue could be located for pictures // Contract crew did not see a flash and were not aware of a fault they may have caused // CYME did put the probable fault location in the general area of where the work was taking place // Cause undetermined with no damage to equipment ~~~ 11/13/2018 ¦ i70604 ¦ Investigative Action